EULEX KOSOVO

TECHNICAL SPECIFICATIONS

Building Management Unit

EULEX Kosovo

April 2026, Pristina

1	GENERAL INFORMATION	4

2	SECURITY CONDITIONS	4

3	SCOPE OF WORKS	5

3.1	CONTRACTOR’S RESPONSIBILITIES	6

3.2	TECHNICAL SUBMISSION AND TIME SCALE	6

3.3	PRIOR TO COMMENCING OF ANY WORK	6

3.4	Final Clearance	6

3.5	WHEN THE CONTRACTOR HAS OBTAINED APPROVAL FROM EULEX	7

3.6	GENERAL WORK REQUIREMENTS	7

x)	A short guide to the personal protective equipment at work (PPE)	11

4	DESCRIPTION OF PROJECT, MATERIALS AND WORKS	16

4.1	Design Submission Requirements	17

4.2	Main Entrance, Buildings and other components Technical Requirements	21

4.2.1	Main Entrance	21

4.2.2	Container Blocks 1,2,3,4,5,6,13,15,17	28

4.2.3	MSO Office Block # 12:	43

4.2.4	Infirmary Block #14:	45

4.2.5	Storage Block # 7:	49

4.2.6	Cafeteria with kitchen appliances	50

4.2.7	Gym Building & Outdoor activities areas	54

4.2.8	Training House	60

4.2.9	Recreation Building	62

4.2.10	MSD Building Refurbishment	65

4.2.11	Fuel Station	76

4.2.12	Other	78

4.2.13	Dismantling of office blocks in old ECM Compound	79

4.3	Infrastructure/Horizontal Services	83

4.4	Electrical Specifications	88

4.4.1	General Electrical requirements	88

4.5	Mechanical Specifications	93

4.5.1	Heating	93

4.5.2	Ventilation System – dining room in Cafeteria	96

4.5.3	Exhaust hood /ventilation for kitchen in Cafeteria	96

4.5.4	Fans /Ventilators for MSD Building / stores&workshops	97

4.5.5	Bathrooms extract fans other areas	97

4.6	General Plumbing/Hydraulic Specifications	97

4.6.1	Water Supply	97

4.6.2	Sewer System and Wastewater Treatment Plant	99

4.6.3	Drainage System	101

4.6.4	Rainwater collection and reuse system Specifications	102

4.7	IT and Communication Specifications	103

4.7.1	Network Infrastructure – Mitrovica Camp	103

4.7.2	CCTV Network Infrastructure:	131

4.8	Fire Detection and Alarm System Specifications	135

4.9	Firefighting Network Specifications – External Overground Hydrants	143

4.10	Solar Photovoltaic System Specifications	147

5	Testing and Commissioning	148

6	Handover	148

# GENERAL INFORMATION

To ensure continuity of EULEX Operations and presence in Mitrovica area EULEX through this project has foreseen Design & Build of a new EULEX Compound for relocation of Formed Police Unit (FPU) from the existing Camp in Mitrovica.

The purpose of the project is to support the mission’s operational sustainability, compliance and readiness for future needs.

Compound is planned to be built in a plot located in Mitrovica-Prishtina road, situated in Cadastral Zone of Shupkovc.

The structures foreseen to be built within the compound are to be temporary in nature. They are to be containerized and modular, allowing for rapid installation, easy relocation, and straightforward dismantling.

This approach ensures flexibility, minimizes long-term impact on the site, and supports changing requirements of the mission.

# SECURITY CONDITIONS

Security Conditions that have to be considered for the performing companies:

- Initially a list of workers and their machinery that they will use during their work will be asked from the contractor.

- The appointed supervisor will meet the contractor’s representative before they start with works and they will consider the security procedures.

- Contractor’s tools which are not going to be used during the weekend will be asked to be securely stored on site (except if they request to  to work during the weekends).

- All the tools shall be locked in tool boxes when not in use (during weekdays and nights).

- The supervisor will check all the working places before the works start and after the works are finished for that particular day (every day).

- No items shall be transported in or out of the site without the express prior approval of the designated EULEX supervisor. The approval, preceded by an inspection of the items to be transported, shall be in writing and will be accompanied by the list of the items approved for transportation to the specific location.

# SCOPE OF WORKS

In this Contract the Contractor shall take responsibility for the design, supply and construction/installation of the works, testing & commissioning, handover all as described hereunder.

EULEX as part of the contract has provided preliminary and conceptual designs for the Compound, Site plans and floor plans for the buildings and services, which are to be developed further by contractor into detailed final designs.

Design Services

- Undertake designs of all phases for the new ECM Compound.

- Prepare detailed drawings, calculations, specifications, and schedules in compliance with applicable codes and standards.

Construction Works

- Execute all building and civil works in accordance with the approved design documents.

- Provide labor, materials, equipment, and supervision required for the complete construction of the ECM Compound.

- Ensure quality control, safety compliance, and adherence to project timelines throughout execution.

Testing & Commissioning

- Conduct comprehensive testing of all installed systems (electrical, mechanical, plumbing, fire safety, and utilities).

- Rectify any defects identified during inspection and testing.

- Provide operation manuals, maintenance schedules, and training to EULEX representatives.

Handover

- Deliver the completed ECM Compound in a fully operational state.

- Submit as-built drawings, test certificates, and warranties.

A Gantt chart outlining  the intended sequence of building completion and the expected milestones is attached to tender dossier.

## CONTRACTOR’S RESPONSIBILITIES

Tenderers will be given the opportunity to visit the site and familiarize themselves with existing conditions.

All tenders will assume to have satisfied themselves concerning all relevant details pertaining to the contract.

Site visit is mandatory.

- Visit of the old EULEX Compound Mitrovica (ECM) including Clarification Meeting

Adress: Street “Ferki Lisica nn. Mitrovica 40000 and

- Visit of New ECM site – Shupkovc, Mitrovica 40000

Tenders that have not attended the mandatory site visit will not be taken into consideration for application.

## TECHNICAL SUBMISSION AND TIME SCALE

Tenders are obliged to include sufficient technical information to allow EULEX to assess the quality of proposal.

Tenders are obliged to state the contract period and the warranty period in their submission and submit a schedule of works in the form of bar chart with regard to the work that needs to be carried out on the site.

This information will be taken into account when proposals are assessed and evaluated.

Gantt chart outlining the intended sequence of building completion and the expected milestones of EULEX provided with tender dossier is to be taken into consideration when preparing the schedule of works.

## PRIOR TO COMMENCING OF ANY WORK

After the approval of the designs and prior to commencing of any work, the contractor shall provide the samples of all materials requested by EULEX representative with the manufacturer specifications that he intends to use, for approval by EULEX designated representative.

The contractor shall submit a complete program which specifies his intended procedure for executing the work in compliance with the above-mentioned requirements.

The contractor shall take his own measurements in accordance with the physical status on the ground before starting of any construction / productions.

## Final Clearance

Upon completion of each section of the works, the Contractor shall clean up the site; remove all temporary buildings, plant if any, and remove debris. He shall level off and fine grade all excavated materials which is surplus to requirements. The whole of the site shall be left in a clean and workmanlike condition to the satisfaction of the Supervisor.

## WHEN THE CONTRACTOR HAS OBTAINED APPROVAL FROM EULEX

All work must be carried out to the complete satisfaction of the delegated representative in accordance with relevant standards and good working practices.

The Contractor shall notify the designated representative, prior to covering any part of the work, which will then be inaccessible for subsequent inspection. Failure to do so will result in exposure of the afore-said works and subsequently reinstatement at the contractor’s expense.

To ensure proper site supervision and quality control, the Contractor shall present:

Site Engineer: Present on site during all working hours, with direct authority over the workforce and responsible for the day-to-day supervision and coordination of the works.

Qualification: Civil Engineer or Architect.

Experience: Minimum 7 years in similar projects.

The Site Engineer shall be English-speaking.

Quality Control Engineer: With proven experience in quality assurance and quality control for construction projects. Responsible for implementing and monitoring the quality control system, conducting inspections and tests, and verifying that works and materials comply with the contract requirements, technical specifications, and applicable standards.

Degree holder in Civil, Building, Architectural Engineering.

7 years work experience in quality assurance and quality control for construction projects

## GENERAL WORK REQUIREMENTS

#### Security and Fire Fighting

The Contractor shall provide and maintain adequate fire extinguishers on the site and areas of high fire risk shall be fenced and signs posted and supplied with specialized fire extinguishers, if necessary. Generators and their batteries and water pumps shall be adequately protected against vandalism and theft. Unless otherwise provided by the Supervisor, the Contractor shall not by his operations obstruct any road or access to other buildings nor break down any fence nor obstruct any drains or water courses, but if such blockages occur he shall at once remove the blockages and repair the breakages.

#### Construction Equipment & Machinery

The Contractor shall provide all necessary sound and adequate equipment, heavy machinery and vehicles machinery vehicles and equipment required for the works that include but are not limited to:

- Trucks of various capacities and volumes

- Crane/s

- Forklift/s

- Excavator/s

- Cherry Picker / Bucket Truck

- Roller/Compactor

- Hand Compactor/s

- Portable Concrete Mixer/s

- Concrete Vibrator/s

- Portable Generators

- Water Pumps

- Adequate hand and power tools suitable for all work activities

- External Scaffolding

- Internal Scaffolding, etc.

The Contractor shall be solely responsible for the employment of skilled and qualified machinery and equipment operators as well as the sufficient and proper maintenance of all machinery and equipment employed on the site.

The Contractor shall be solely responsible for the adequate lighting where work is being executed at night and shall provide and install any additional lighting which the Supervisor may require in order to watch and supervise the works and carry any testing and examination of materials. Materials available on the site or materials made available or supplied by the Contractor shall be used solely for the execution of the works. The Contractor shall minimize the pollution of and disturbance to roads and other places on and around the site. No trees or other vegetation shall be removed except with the express permission of the Supervisor. The Contractor shall ensure that access is provided to all buildings and properties adjacent to the site for the duration of the contract.

All temporary buildings erected by the Contractor upon the sites and the layout of the buildings and the site, shall comply with laws and all local by-laws in so far as they are applicable.

The Contractor shall be absolutely and solely responsible for the safety and security of temporary works and for the equipment in connection therewith which may be erected or provided for the carrying out of the contract and for the execution of the works. This provision shall be applicable to all temporary works and equipment whenever provided and erected by the Contractors for the purpose of or in connection with the works. Examination and acceptance by the Supervisor of the Contractor’s temporary works or of the drawings connected therewith shall not absolve the Contractor from his responsibility for those works and his liability for the consequences of any failure.

#### Water Supply

EULEX will allow use of water within the Compound during the construction works where and if possible; however, connection points are to be previously authorized by the Contracting Authority. Water consumption during the works are not to be charged.

Contractor is to undertake all arrangements if provision of pumps, storage tanks etc is required.

#### Electric Power Supply

EULEX will allow the Contractor the connection of electricity during their works to a specific connection point if available. Power consumption during the works is not to be charged. However, the Contractor is to provide all wiring, lamps, switches, fuses, receptacles, etc., as may be required for his work. Temporary power and light circuits are to be thoroughly insulated and waterproof. The temporary power and light system are to be subject to the inspection and approval of the appropriate authority. All the used electrical materials for the temporary connection established by the contractor are to be CE mark.

If there is no electrical power supply at the location at the time of the project contractor is to arrange for its own generators.

    - Use of the Site

The Contractor shall restrict his activities to within the sites and shall avoid entry on to any other lands except where the Contractor has made his own arrangements for such entry or the owner has arranged for this entry. Any trespass, damage or claims arising from such entry shall be the sole responsibility of the Contractor, who shall hold the Contracting Authority indemnified against all claims arising from such trespass or damage.

Environmental Management:

The contractor shall submit an Environmental Management (EM) Plan demonstrating:

Environmental protection measures.

Waste management procedures.

Pollution prevention controls.

Noise and dust mitigation measures.

Resource and energy management practices.

Environmental monitoring and reporting procedures.

Compliance with applicable environmental regulations.

    - Weather Conditions

Without limiting his liabilities, the Contractor shall make suitable arrangements to protect the works and the temporary works, against the effects of the weather.

    - Protection of Existing Works and Services

The Contractor shall explain himself with the position of all existing services such as sewers, surface water drains, cables for electricity and telephone, telephone and lighting, poles, water mains, heating supply pipes and the like, before commencing any excavation or other works likely to affect the existing services. The Contractor will be held liable for all damages to road, main pipes, electrical cables, lines or services of any kind caused by him or his Sub-Contractors in the execution of the works. The Contractor shall make good any damage without delay and, if necessary, carry out any further work ordered by the Supervisor. The Contractor shall indemnify the Contracting Authority against any claims in this respect. In all case where such works or services are exposed, they shall be properly shored, hung up or otherwise protected. Special care shall be exercised in filling and compacting the ground under mains, cables, etc., and not to cover up any water meters, stopcock boxes and similar items. Installations adjacent to the works shall be kept securely in place until the work is completed and shall then be made as safe and permanent as before.

    - Temporary Buildings for Use by the Contractor

The Contractor shall provide and maintain in a perfectly usable and watertight condition, on land in possession of the beneficiary or such lands as he may acquire for the purposes of the works with the approval of the Supervisor, such temporary buildings of timber, galvanized iron, or other suitable material as may be necessary for his general use in connection with the works. As well as buildings for the temporary accommodation of any labor, and for the use of the persons employed by him. Before constructing such buildings he shall supply to the Supervisor a plan or plans showing their positions and nature which shall be in all respects to the approval of the Supervisor.

Prior to preparing his Tender, the Contractor shall satisfy himself as to what will be required especially with regard to labor accommodation.

The cost of providing temporary buildings for use by the Contractor shall be spread over the works.

    - Health, Safety and Accidents

The Contractor is obliged to observe all the stipulated measures pertaining to fire protection, protection at work as well as hygienic and technical conditions such as Fire Protection Regulations Rule Book on general Measures and Normative of Protection at work concerning building facilities intended for the work and other subsidiary premises. The Contractor shall ensure, so far as is reasonably practicable and to the satisfaction of the Contracting Authority, the health, safety and welfare at work of his employees including those of his Sub-Contractors and of all other persons on the Site.

His responsibilities shall include: the provision and maintenance of equipment and systems of work must be safe and without risks to health; the execution of suitable arrangements for ensuring safety and absence of risks to health in connection with the use, handling, storage and transport of articles and substances; the provision of protective clothing and equipment, first aid stations with such personnel and equipment as are necessary and such information, instruction, training and supervision as are necessary to ensure the health and safety at work of all persons employed on the works all in accordance with Laws and all local By- Laws;

- Designation of a Health and Safety Officer:

Who shall have relevant professional qualifications and certifications with knowledge of safety regulations, and experience of safety precautions on similar works and who shall advise on all matters affecting the safety of workman and on measures to be taken to promote such safety; the provision and maintenance of access to all places one the site in a condition that is safe and without risk of injury; the provision of adequate water-borne sanitation, refuse collection and disposal, complying with the Laws and all local By-Laws and to the satisfaction of the Supervisor, for all site offices, workshops erected on the camp site; the provision of suitable latrines and other sanitary arrangements at the site where work is in progress to the satisfaction of the Medical Officer in the area and of the Supervisor; the execution of appropriate measures in consultation with the appropriate Public Health Authority to control within the site; reporting details of any accident to the Supervisor as soon as possible after its occurrence; the provision and maintenance of adequately equipped first aid station on the site of the works.

Health and Safety Management:

The contractor shall submit a comprehensive Health and Safety (H&S) Management Plan demonstrating:

Health and safety policy and objectives.

Risk assessment methodology.

Site safety procedures.

Emergency response arrangements.

Worker training and competency management.

Monitoring and reporting procedures.

Compliance with applicable H&S legislation and standards.

### A short guide to the personal protective equipment at work (PPE)

What is PPE?

PPE is defined in Regulations as ‘all equipment (including clothing affording protection against the weather) which is intended to be worn or held by a person at work and which protects him against one or more risks to his health or safety’, e.g. safety helmets, gloves, eye protection, high-visibility clothing, safety footwear and safety harnesses..

What do the Regulations require?

The main requirement of the PPE at Work Regulations is that personal protective equipment is to be supplied and used at work wherever there are risks to health and safety that cannot be adequately controlled in other ways. The Regulations also require that PPE:

• is properly assessed before use to ensure it is suitable;

• is maintained and stored properly;

• is provided with instructions on how to use it safely; and

• is used correctly by employees.

Assessing suitable PPE

To allow the right type of PPE to be chosen, carefully consider the different hazards in the workplace. This will enable you to assess which types of PPE are suitable to protect against the hazard and for the job to be done. Ask your supplier for advice on the different types of PPE available and how suitable they are for different tasks. It may be necessary in a few particularly difficult cases to obtain advice from specialist sources and from the PPE manufacturer. Consider the following when assessing whether PPE is suitable:

• Is it appropriate for the risks involved and the conditions at the place where exposure to the risk may occur? For example, eye protection designed for providing protection against agricultural pesticides will not offer adequate face protection for someone using an angle grinder to cut steel or stone.

• Does it prevent or adequately control the risks involved without increasing the overall level of risk?

• Can it be adjusted to fit the wearer correctly?

• Has the state of health of those who will be wearing it been taken into account?

• What are the needs of the job and the demands it places on the wearer? For example, the length of time the PPE needs to be worn, the physical effort required to do the job and the requirements for visibility and communication.

• If more than one item of PPE is being worn, are they compatible? For example, does a particular type of respirator make it difficult to get eye protection to fit properly?

The hazards and types of PPE

Eyes

Hazards: chemical or metal splash, dust, projectiles, gas and vapors, radiation.

Options: safety spectacles, goggles, face shields, visors.

Head

Hazards: impact from falling or flying objects, risk of head bumping, hair entanglement.

Options: a range of helmets and bump caps.

Breathing

Hazards: dust, vapor, gas, oxygen-deficient atmospheres.

Options: disposable filtering face piece or respirator, half- or full-face respirators, air-fed helmets, breathing apparatus.

Protecting the body

Hazards: temperature extremes, adverse weather, chemical or metal splash, spray from pressure leaks or spray guns, impact or penetration, contaminated dust, excessive wear or entanglement of own clothing. Options: conventional or disposable overalls, boiler suits, specialist protective clothing, e.g. chain-mail aprons, high-visibility clothing.

Hands and arms

Hazards: abrasion, temperature extremes, cuts and punctures, impact, chemicals, electric shock, skin infection, disease or contamination.

Options: gloves, gauntlets, mitts, wrist cuffs, armlets.

Feet and legs

Hazards: wet, electrostatic build-up, slipping, cuts and punctures, falling objects, metal and chemical splash, abrasion.

Options: safety boots and shoes with protective toe caps and penetration-resistant mid-sole, gaiters, leggings, spat.

Training

• Make sure anyone using PPE is aware of why it is needed, when it is to be used, repaired or replaced and its limitations.

• Train and instruct people how to use it properly and make sure they are doing this.

• Because PPE is the last resort after other methods of protection have been considered, it is important that users wear it all the time they are exposed to the risk. Never allow exemptions for those jobs which take ‘just a few minutes’.

• Check regularly that PPE is being used and investigate fully any reasons why it is not. Safety signs can be useful reminders to wear PPE

Maintenance

Make sure equipment is:

• well looked after and properly stored when it is not being used, for example in a dry, clean cupboard, or in the case of smaller items, such as eye protection, in a box or case;

• kept clean and in good repair - follow the manufacturer’s maintenance schedule (including recommended replacement periods and shelf lives). Simple maintenance can be carried out by the trained wearer, but more intricate repairs should only be done by specialists. Make sure suitable replacement PPE is always readily available.

# DESCRIPTION OF PROJECT, MATERIALS AND WORKS

- Information on the plot / existing condition:

Overall net surface after the plot is fenced is estimated to be 28 930m2.

The plot at the time of commencement of this contract shall be handed over to the selected contractor in the below described condition:

- Fenced with T walls and metal fence min 3-meter height around the whole perimeter. There shall be two temporary gates manually operated to be used during the construction works to access the Compound. Once the new entry gate is developed the main temporary gate will be replaced with T walls. Leaving only the new main entry and emergency exit.

- The site will have lights and cameras installed around the whole perimeter.

- Also the outer perimeter underground trenches with manholes will be in place. With two OD 40mm and two of OD 75mm ducting pipes positioned from one manhole to the other and exit to each metal pole in the perimeter.

- 630Kva positioned as indicated in designs presented with electrical meter for the Compound.

- 2 water meters in place ( for water supply network and for external hydrants)

- There shall be a drainage manhole positioned at the lowest level of the compound with discharge to Sitnica river.

There is a sewerage connection nearby the Compound perimeter but all is discharged into Sitnica River without any treatment. EULEX will not use such connection for the sewerage and any sewerage discharge from the Compound into the river is to take place after treatment of wastewater.

Ground will be levelled/sloped and compacted at 80 MN/m2.

Provisional site layout (site leveling plan) will be shared with contractor as part of preliminary designs.

Leveling on the design show final asphalt level intended to be achieved, however it is subject to revision with final designs of the compound, coordinated with all disciplines/infrastructure.

- Preliminary and conceptual designs

Preliminary site plans and conceptual building designs presented as part of this dossier have been designed by Building Management Unit of EULEX with the input of other technical units and operational components requirements focused on operational needs, functionality, efficiency and security.

The Compound is organized into distinct zones to ensure efficiency and clarity of use: accommodation zone, training zone, support services zone, cafeteria zone and security zone.

Each zone is to meet its operational purpose while contributing to the overall coherence of the compound.

Pathways/ roads are designed to connect all facilities to ensure smooth movement and accessibility.

Controlled entry points have been organized as per Security Requirements of the mission with the Compound perimeter definition.

All structures proposed within the compound will be temporary in nature. They will be containerized and modular, enabling rapid installation, easy relocation, and straightforward dismantling. This approach provides flexibility, minimizes long-term site impact, and accommodates the evolving requirements of the mission.

The structures are based on standard designs used at other EULEX locations in Kosovo, allowing for streamlined maintenance procedures, common spare parts, and consistent operational practices.

For engineering calculations, the maximum occupancy of 200 persons shall be considered as the design basis.

Occupants are to be assumed present continuously (24 hours per day, 7 days per week) for all relevant engineering design and operational considerations.

## Design Submission Requirements

Detailed designs for all phases are to be prepared and presented by contractor based on preliminary designs and technical requirements hereunder presented by Contracting Authority.

Prior to commencing preparation of any design contractor is to carry out its own study of existing site conditions and verification of the preliminary drawings, including site leveling.

The Contractor’s complete detailed designs, calculations, specifications and drawings shall be submitted, in English language, for approval, as they are developed, up to final approval (PDF, ArchiCAD or AutoCAD, Word, Excel, MS Project, etc).

Final submission is to include also 3 bind hard copies (Albanian language) and 1 soft copy.

Final Hard Copy sets including one soft copy will be submitted to Municipality by EULEX for Building Permit required as part of the process.

Any approval granted shall not absolve the Contractor of their full responsibility for the design.

Designers/engineers engaged in the process are to be licensed to operate in their field of expertise, depending on the engineering discipline, in accordance with Kosovo law (License A) or international equivalent license.

The following are gross and net m2 from preliminary designs of buildings presented and planned to be constructed within the ECM Compound.

|  |  |  | Gross m2 | Net m2 |
| --- | --- | --- | --- | --- |
| Buildings: |  |  |  |  |
| Container Block 1- Platoon Accommodation Block |  |  | 610.00 | 555.00 |
| Container Block 2 – (identical with Block 1) |  |  | 610.00 | 555.00 |
| Container Block 3 - (identical with Block 1) |  |  | 610.00 | 555.00 |
| Container Block 4 – Female Accommodation Block |  |  | 251.00 | 223.00 |
| Container Block 5 – Commander Accommodation |  |  | 339.00 | 309.00 |
| Container Block 6 – Offices |  |  | 475.00 | 431.00 |
| Container Block 7 – Storage |  |  | 103.00 | 97.00 |
| Building 8 – Recreation Building |  |  | 129.00 | 120.00 |
| Building 9 – Training House |  |  | 196.00 | 188.00 |
| Building 10 – Gym |  |  | 527.00 | 490.00 |
| Building 11 – Cafeteria |  |  | 385.00 | 346.00 |
| Container Block 12 – MSO |  |  | 136.00 | 123.00 |
| Container Block 13 – Reception |  |  | 89.00 | 81.00 |
| Container Block 14 – Infirmary |  |  | 174.00 | 162.00 |
| Container block 15 – Reserve Block |  |  | 814.00 | 747.00 |
| Existing MSD Building 16 |  |  | 985.00 | 905.00 |
| Container Block 17 – Cleaning Contractor |  |  | 128.00 | 114.00 |
| Metal Covers Structures: |  |  |  |  |
| Vehicle Entry metal cover dim. 22x 7.5m |  |  |  |  |
| Vehicle parking Cover “A” 27.5x7m |  |  |  |  |
| Vehicle parking cover “B” 31.5x6m Vehicle Parking cover “C” (2x) 6x6m Other: Vehicle and Pedestrian Entry – Security Systems Fuel Station Vehicle Inspection Pit Helipad |  |  |  |  |

- Architectural Designs:

From provided preliminary and conceptual designs of the Compound and buildings contractor is to further develop detailed designs of the Compound:  site plan, building floor plans, sections, elevations, details, coordination with other discipline designs.

- Civil / Structural Engineering Designs:

Structural analysis and calculations, static calculations, structural element detailing, roads/pavement and associated plans and drawings.

- Mechanical Designs (HVAC):

Systems design and calculations, preparation of plans and drawings, developed to ensure thermal comfort, indoor air quality, and energy efficiency.

- Electrical Engineering Designs:

Load and capacity calculations, power distribution design and plans for the compound and buildings/structures, lighting system designs, inclusive of emergency lighting provisions, etc.

- Hydraulic / Plumbing Designs:

Water Supply Systems:

Design and sizing of water supply systems, including capacity and pressure calculations to ensure adequate flow. Compound-wide water networks from the water meter, cold and hot water distribution systems, and pumping systems with storage tanks provided as backup supply.

Sewerage Systems:

Design of compound sewerage network system including the wastewater treatment plant, with discharge to the Sitnica River after treatment. Building-level sewerage systems (toilets, sinks, floor drains, grease trap etc.),including sizing and capacity calculations.

Stormwater Drainage:

Design of site-wide stormwater drainage systems, including sizing and capacity calculations, roof drainage systems, and associated components such as oil separators, etc

- IT and Communication Designs / Safety and Security Systems:

Design of network infrastructure.

Outdoor fiber optic backbone cabling between Data Center and buildings, Indoor Horizontal Structured Cabling from the Intermediate Distribution Frame (IDF) network cabinet to end‑user dual RJ45 outlets.

Including partial routing/cabling for Internal Cameras, Security entrance, etc as per preliminary designs and specifications.

- Fire Alarm System:

Site Fire Alarm layout plan, Fire Alarm floor plans, Network diagram, details and schedules as per details given herewith in this document.

Fire Protection Report.

- Firefighting network - external hydrants:

Design of external fire hydrant systems, including hydrant location and spacing, hydraulic sizing and flow calculations, pipe network routing, connection to water supply sources, and preparation of plans and drawings in accordance with applicable fire safety standards.

- Environmental and Sustainability Systems:

Solar photovoltaic system of 260kWp design

Rainwater collection and reuse system design

Building Physics and Energy Efficiency Report

Design team to consist of but not limited to:

Architect

Qualified and Licenced Architect (A)with minimum 7 years of experience in the design of similar projects.

Civil Engineer (Construction/Structural)

Qualified and Licenced Civil Engineer (A) with minimum of 7 years of experience in the design of similar projects.

Civil Engineer (Hydro)

Qualified and Licenced Civil Engineer (A) with minimum of 7 years of experience in the design of similar projects

Mechanical Engineer

Qualified and Licenced Civil Engineer (A) with minimum of 7 years of experience in the design of similar projects

Electrical Engineer

Qualified and Licenced Civil Engineer (A) with minimum of 7 years of experience in the design of similar projects

CIS Specialist/Engineer

Relevant qualifications and experience in communications and information systems designs.

## Main Entrance, Buildings and other components Technical Requirements

Detailed designs will be presented by contractor and approved by Contracting Authority as per point 4.1 above and as approved the construction works can commence on site.

The Contractor shall:

- Execute all building and civil works in accordance with the approved design documents, specifications, and applicable codes and standards.

- Provide all labor, materials, plant, equipment, temporary works, and supervision necessary for the complete construction and commissioning of the ECM Compound.

Labor shall consist of but not limited to: General construction workers, electricians, plumbers, welders, HVAC mechanical workers, heavy machinery operators, other as required for completion of the project.

- Coordinate all construction activities to ensure proper integration of the various compound components.

- Implement and maintain appropriate quality assurance and quality control procedures throughout the execution of the Works.

- Comply with all health, safety, environmental, and security requirements applicable to the Project.

- Ensure that all works are completed within the approved project schedule and in accordance with the Contract requirements.

- Obtain all required inspections, testing, approvals, and certifications related to the construction works.

Below are specifications of Main Components of the Compound:

### Main Entrance

The main entrance to the Compound shall comprise of vehicle entrance/exit and pedestrian entrance/exit.

The vehicle entrance is to be equipped with:

- High Security Automated Speed Bi-folding Gate

- Under Vehicle Surveillance System (UVSS) and 2xPlate Recognition Cameras

- Road barriers entry and exit

- Road blocker

- Access Control for vehicles and pedestrians both on entry and exit.

- Video Intercom outdoor unit, displayed in reception.

Entry Procedure:

For both EULEX and visitor vehicles, access control is to be managed by the guard stationed at the reception. As a vehicle approaches the entrance, the guard opens the main gate from the reception.

Once the gate is opened, the vehicle proceeds through the Under Vehicle Scanning System (UVSS), where the vehicle is scanned.

The reception guard reviews the real-time scan images on the monitoring screen and either grants access or triggers an alarm in case of a detected threat.

Simultaneously, the Automatic Number Plate Recognition (ANPR) camera captures and records the vehicle’s license plate, registering it in the system.

For EULEX personnel, after the vehicle is cleared through the UVSS by Security Guard (the guard swipe the card clears access in reception),  the driver then swipes their access card in the card reader positioned at the driver side.

Upon successful authentication by the access control system, the barrier is raised, the road blocker is lowered, and the vehicle is permitted to pass when the traffic light turns green.

For visitors, access authorization is granted by the receptionist/guard, who activates the required systems to allow the vehicle to proceed further.

Exit Procedure:

The exit process follows the same sequence in reverse order. Vehicles exit the facility under controlled conditions, with the relevant systems (barrier, road blocker, and traffic light) activated accordingly to ensure safe and secure departure. UVSS is not part of the exit procedure except the ANPR where camera captures/registers the plate numbers of vehicle exiting.

#### High Security Automated speed bi-folding gates

Contractor is to design, provide and install automated high speed and secure bi-folding gate as main entry/exit to the compound.

The gate is to be operated by the guard located in the reception room.

Clear opening of the gate after both wings are folding is to be 6 meters, height 3m.

Wings are to be operated individually, separate motors, and when one side is folding free opening is to be 3 meters clear.

Design to be presented for approval prior to ordering.

Trackless automated bi-folding speed gates comprise of a drive mechanism to control the opening and closing of a bi- folding set of gates, no height restrictions. The mechanism is to control both leaves, producing smooth and fast action. The speed of opening and closing is essential for the security of the premises, approximately 1m per second.

Hydraulic design, low maintenance with minimal moving parts.

Metal structure with security-mesh, including centre stop.

Security mesh designed to meet specifications for secure compounds, anti-climb design. Mesh panels with wire welded at every intersection.

Galvanized and powder coated. Color: similar to existing fence on site/blue.

Integrated with other security systems.

Equipped with traffic lights (green/red) and sensors both on entry and exit.

Sample picture – for illustration purpose

#### Under Vehicle Surveillance System (UVSS) complete set including Plate Recognition Cameras

After entering the Compound, the vehicle is to pass through Under Vehicle Surveillance System.

Contractor is to provide and install under vehicle surveillance system (UVSS) in order to scan, inspect, and digitally record the underside of vehicles, which will be monitored by the guard located in the reception.

Prior to commencing the works on site the contractor is to review the EULEX preliminary design and present final design in compliance with manufacturer instructions for installations and requirements foreseeing all the required connections to the infrastructure.

Below are minimum criteria for the system set.

Fixed under Vehicle Detection System:

- IP 68 /All-weather performance

- High-speed line-scanning camera /LED illumination

- High-resolution color image

- Weight capacity 50T

- Real-time surveillance / recording function.

- Speed of vehicle ≤ 30km/hrs

- Duration of use: 24/7

- Anti-Fog function

- Applicable to variety of vehicles, wide vision

- License plate registration cameras included, vehicles entering and exiting shall be registered in the system.

The system to come as a set with Line scanning cameras, distribution box, compresses bottom groove, operating system, computer/monitor, underground loops system which trigger the scanning, license plate cameras etc.

Sample picture of line scanning cameras

#### Road barriers

Two road barriers are to be installed, entrance and exit.

Length: 3.3 – 3.5meter subject to final design when all security equipment are determined.

With built-in control unit, adjustable speed and anti-crush safety function.

Operation is to be guaranteed in the event of power outages with backup battery.

Compatibility with control systems.

Access granted through card readers on entry/exit or guard located in the reception.

#### Road blocker

Road Blocker is to be installed to prevent unauthorized vehicles from accessing the area and ensure the highest level of protection. Access granted through card readers on entry/exit or guard located in the reception ( as per entry and exit procedures).

The Contractor is to supply and install one hydraulic operated electrical road blocker, (entrance/exit of the compound).

Road blocker is to be facing towards incoming traffic.

Contractor is to provide design, technical specifications and technical proposal for the same.

The installation frame should be fitted into a fully reinforced foundation with drainage points to connect to suitable soakaway/drainage (depending on depth of installation technical solution is to be sought), if required pump to be included as well in the design.

- Raise between 0.8 – 1m / length 5 meter.

- LED indicator on front

- Battery back-up for power off situation

- Crash / Impact Rating Designed and produced to withstand M50 P1 (K-12)

- Manuel Control Button Unit

- Compatible with any access control system.

- Light indicator (red/green)

- High visibility with yellow and black diagonal stripes on impact surface. Reflective marking.

#### Access Control

Both vehicle and pedestrian entrance are to be equipped with access control system for EULEX personnel/vehicles.

Vehicle access control card readers shall be mounted on stainless steel (inox) poles, positioned at a height suitable for use from the driver’s side window of a vehicle. Card readers shall be installed at both entry and exit points and fully integrated into the overall access control system, operating in accordance with the defined vehicle entry and exit sequence and system interconnections. There shall be also and authorisation point button/reader situated in the reception where clearance after UVSS check is given to the system.

Pedestrian access control and entry:

Visitors will access the Compound with access granted by the receptionist. Video intercom outdoor unit is to be provided and installed for the visitor with display positioned at the reception. Once the visitors activate the bell the receptionist will be able to identify and conversate with the visitors and only then grant or deny access.

For EULEX personnel:   ZKTec card reader x 2 (for in and out), electromagnet / electric lock, switch controlled from reception,  are to be provided and installed for both main pedestrian entry door and also the door nearby the reception.

EULEX Personnel can access the compound by swiping the cards, while visitors are granted access with the doors operated by EULEX guards.

Metal Works:

- Roof cover

A steel metal cover shall be provided for the vehicle entry with overall dimensions of 22.0 m (length) × 7.5 m (width), including all structural members, roofing, foundations, and finishes, complete and ready for use.

Prior to commencing any fabrication or manufacturing work, the Contractor shall:

- Prepare and submit detailed design drawings.

- Provide static/structural calculations demonstrating adequacy of the proposed steel sections for all applicable loads (dead, live, wind, snow).

Quality of the steel used for the steel structure is to meet the requirements of the following standards EN 10 025/S235JR.

All the steel elements are to be cleaned first and painted with anti-rust/base coats of paint in two layers; painting of any welding spots is to be carried out after assembling/welding on site also in two layers.

Final painting to be done with oil paint, color blue, in two layers, reaching a uniform color throughout the entire structure.

Reinforced foundation of the main columns: 10 cm sand bed is to be provided/placed and foundations are to be filled using concrete C 30.

Roof covering is to be done using trapezoid pre painted corrugated metal sheet, 0.55mm thick, color RAL 9002, including roofing ridge cap and snow guards, installed over metal purlins.

Roof is to be completed with horizontal and vertical gutters installed, including flashings.

All parts (union brackets, running outlets, stopend internal, pipe clips, offset bend, etc) are to be of the same material as the gutters and downpipes.

There shall be sufficient number of LED lights installed under the vehicle cover to illuminate the area. Refer to electrical requirements for the Compound and electrical designs to be developed.

- Pedestrian doors / Fence

Pedestrian doors are to be manufactured and installed as per integrated within the metal fence.

All profiles / the structure of the doors are to be made rust free; primer painted in two layers with anticorrosive paint.

Final painting of metal profiles is to be done with oil paint, color blue in two layers, reaching a uniform color of the entire door structure. Same color as the existing fence on site.

- New fence:

Metal fence is similar to the existing fence on site and consists of vertical metal supporters, 60x100x5mm for which foundations are to be dug each 3 m, dimension 60x60x70cm.

10 cm sand bed is to be provided/placed and foundations are to be filled using concrete C 30 (60X60X60cm).

Fence panel consists of horizontal metal profiles 60x40x3mm and vertical/diagonal profiles 25x25x2mm as per detailed drawing provided.

On top of diagonal profiles steel pikes 4x70mm are to be welded. The fence is equipped with V profiles on top of each column and concertina wire of 60cm diameter is to be provided and installed.

- Polycarbonate cover:

Partially the installed fence will be covered with the polycarbonate cover / exterior.

Polycarbonate sheets should be of twin wall rectangular cell structure, 6mm thickness, blue in color, weather and UV resistant properties. Fixing of the polycarbonate sheets to the fence metal profiles is to be done with self-tapping or self-drilling screws, every approx. 43cm, fitted with conical washer and a special shaped integral rubber gasket.

Both screws and washers are to be corrosion resistant (galvanized or stainless steel).

Sheets are to be connected in-between with PC - H profiles specially designed for connection of PC sheets.

The edges of the sheet are to be sealed with U polycarbonate profiles giving a rigid and neat finish to the panel and preventing the dust, water and bugs to get access to the hollow space.

Other: Angular and linear impact barriers are to be installed around the panels of security systems and corner of the buildings

Steel tube elements diameter 60mm, 3mm thickness.

Height 500mm - rectangular 500mm in both sides

Height 500mm – linear 1000mm

Sample photo of barriers

Note: Any materials or works for installation of security systems, trenches/manholes/drainage for road blockers/power supply or IT cabling is to be part of the security system units pricing for the overall system to be functional.

Power supply connection to be established at the Reception Building Panel.

For groundwork refer to point 4.3 hereunder.

Asphalt, curbstones, and pavements works for the entry/exit are to be priced under overall Compound pricing for those positions BOQ# 02.

### Container Blocks 1,2,3,4,5,6,13,15,17

Blocks comprising office, ablution, and storage containers shall be constructed to accommodate personnel, office functions, and storage requirements.

Hereunder are the technical specifications for the characteristic accommodation and office blocks to be constructed (thereof Block 1, 2, 3, 4, 5, 6, 13, 15,17).

Construction of Container blocks is to be done using secondhand structures which are to be provided to Contractor by EULEX.

The container structures (refurbished office container steel frames with floor steel structure) will be transported and made available to contractor on site for them to proceed with positioning and construction. Before installation contractor is to dismantle roof panels and replace them, which was left installed for stable transportation of structure on site only.

20’ steel structure – photo for illustration purpose

The exterior and interior dimensions of typical single container structure are given below:

- 20’ container exterior dimensions: 244x605cm - height 261.5cm

- 20’ container interior dimensions: 222x585- height 230cm

- 10’ ablution container exterior dimensions: 244x255cm height 261.5cm.

- 10’ ablution container interior dimensions:   225x232cm height 230 cm.

#### Foundations of blocks:

All container blocks are to be positioned over reinforced strip foundations. Foundations shall be of depth and width suitable for the imposed loads and temporary nature of the installation, formed on firm, level ground. Contractor shall design/calculate and present for approval foundation design prior to commencing any works on site.

Grounding of the building is to be foreseen.

#### Construction/Installation works:

Containers steel structure, walls and ceiling panels.

Provided container steel structures are to be positioned over strip foundations as per building layouts. They are to be welded in between on the upper and lower beams. Creating the skeleton structure of the blocks whether ground plus first floor or only ground floor.

The wall polyurethane sandwich panels t=50mm are to be provided and installed in existing metal structure of office container as per set up of floor plans double/single/triple containers:

• Sandwich panel thickness: 50 mm.

• External side plane sheet thickness: 0,5 mm.

• Internal side plane sheet thickness: 0,5 mm

• Color RAL 9002

Depending on width of panels in general there are 5+ panels on the long side and 2+panels on the short side (depending also on the width of the panel). Panels are installed in sequency and inserted along the sliding lower guides. They are to be fixed with suitable plates.

For the ceiling in office containers the polyurethane sandwich t=100mm panels are to be provided and installed in the existing metal structure. The panels must be well sealed with sealant from the top side so that the ceiling is completely waterproof:

• Sandwich panel thickness: 100 mm.

• External side plane sheet thickness: 0,5 mm.

• Internal side plane sheet thickness: 0,5 mm

• Color RAL 9002

Upper, lower and corner finishing profiles (skirting) are to be provided and installed at the corner/joint of panels.

Containers floor layers:

The structure provided by EULEX will have the steel floor structure (in general steel profiles each 60cm) and the galvanized sheet installed in between which supports the layers.

To be provided and installed for each container floor are:

- Mineral wool thickness 100 mm (Fire classification: DIN EN 13 501-1;) among steel transverse supports.

- Plastic sheet 0.2mm

- Plywood th=20mm for the office containers

-Water-resistant plywood th=20mm for the ablution containers (1st floor)

Final coat:

Homogenous PVC 2.0mm thick, commercial use, EN 649, classification as per EN 685 - Class minimum 33, areas with heavy traffic, including skirting around the perimeter.

- PVC floor is to be raised 15 cm in ablution units (1st floor)

-Colour to be chosen by EULEX Representative.

Corridor floor structures:

Ground floor corridor:  is to be of reinforced concrete floor with flat uniform finishing, thickness 100mm, C20/25, and concrete screed of 40mm.

PVC foil 0.2mm in one layer under reinforced concrete floor overlapping at minimum 100mm in joints, as per manufacturer's instructions.

Thermal insulation “styrodur”, in thickness of 120 mm (2x60mm), layer under PVC foil.

1st floor structure: First floor corridor structure is to be constructed of metal profiles 60x40x3mm each 60cm crosswise, and those of 40x40x2.6mm lengthwise, including L profiles 50x4mm lengthwise on both sides of the corridor and 100x60x4mm in front of staircase, as per designs provided.

All metal profiles are to be made rust free, primed with two layers of an appropriate anticorrosive paint.

The surface preparation of the construction must start with cleaning the elements.

Plywood 20mm is to be used over which final layer is positioned.

Final layer: Llaminate flooring for the corridors, suitable for commercial use, resistant to scratches and water, with 5mm sponge under-layer, t=8mm. With appropriate skirting profiles throughout the building and aluminum skirting at offices entrance/building entrance.

Samples to be provided for approval prior to installation.

Ablution unit flooring – ground floor:

Final layer: ceramic tiles R10

Concrete screed 4cm

Reinforced concrete slab 100mm – mesh Q335. Plastic sheet 0.2mm.

Gravel 0-31mm compacted.

Ablution unit flooring – 1st floor:

Final layer: PVC layer 2mm, 15cm raised to the walls

Waterproof plywood 20mm, plastic sheet 0.2mm and mineral wool 100mm.

Ceiling in corridors:

Suspended ceiling is to be provided and installed of lightweight panels made of mineral fiber and suspension grid made of metal channels in the shape of an upside-down "T", suspended on wires from the overhead structure.

Dimensions 600x600mm, white in colour, complete with all the necessary fixtures.

Samples to be provided for approval prior to installation.

For the 1st floor corridor a supporting timber structure of 80x50mm supported in roof trusses is to be provided and installed including 100mm mineral wool insulation, plastic sheet of 0.2mm, overlapped.

Also, the ceiling above interior staircase consists of rectangular profiles 100x600x4mm including L Profiles 50x4mm lengthwise on both sides of the staircase as per designs provided.

PVC Doors and Windows:

- Office doors:

PVC – framed doors with full solid panels and no glass.

Frames shall be firmly fixed to the container wall panel with correct alignment and tight sealing with skirting around the frame on both sides. Each door shall be provided complete with hinges, handles, locks, and all accessories necessary for proper operation. Minimum three keys shall be provided for cylinder of each door. Dim: 95/210cm.

- PVC Office Windows:

PVC Framed window, tilt-and-turn opening, glazed with double glass 4+16+4mm. U≤1.4 W/m²K

The joint line between window and wall is to be covered with PVC or white aluminum color skirting ┴ profile from the inside.

Window is to be equipped with mosquito net on an independent frame with mechanism for opening and closing as needed.

All windows are to be fitted with PVC window ledges (outside) as per sample photo.

Venetian Blinds for offices and corridor windows:

- Pre painted metal headrail and bottom rail for 25mm slats.

- 25mm aluminum slats (color to be chosen by EULEX Representative)

- Ladder made of polyester yarn.

- Lift cord used to lift the slats and bottom rail to the desired level.

- Flexible wand with m/rope to arrange/rotate the slats (180º).

Vertical Blinds for corridor long windows:

- Ceiling installation/Head rail with stainless steel spacers.

-127mm fabric vertical strips (color to be chosen by EULEX Representative).

-Bottom weights with chain.

-High quality louvre hooks that blend with the fabric of the blinds.

-Tilt and traveling wand, chain operated tilt mechanism.

- Main Entry Doors, emergency exit doors and corridor windows:

Depending on the buildings designs dimensions differs.

Please refer to preliminary designs for dimension required for each block.

They are to be exterior PVC Framed Doors / windows.

Double glazed:4+16+4mm glass. U≤1.4 W/m²K

All windows to be equipped with mosquito net on an independent frame with mechanism for opening and closing as needed.

The joint line between window/door and wall is to be covered with PVC or white aluminium color skirting ┴ profile from inside.

Emergency doors are equipped with emergency exit hardware/ panic push bar with possibility to lock with the key from outside and hydraulic door closure.

- Reception sliding windows:

One (1) exterior and one (1) internal aluminum sliding window shall be supplied and installed in the reception room. The windows shall be smoothly and easily operable to facilitate direct communication with visitors accessing the compound both by vehicle and on foot. Dimension: 200x120cm. Preferred color white to match to the overall building design.

Easy one hand operation. Locking device especially for the exterior window.

Staircases: Interior and Emergency:

One (1) interior staircase and one (1) emergency exit staircase shall be provided for blocks consisting of G+1 floors.

Both staircases shall be fabricated entirely from steel/metal profiles.

Structural drawings shall be prepared by the Contractor and submitted for approval prior to any manufacturing or fabrication work.

All dimensions, levels, and site conditions shall be verified on site prior to final detailing and manufacturing.

Maximum riser (rise) height: 170 mm

Tread (step) depth: 300 mm

Interior Staircase:

- Wooden treads, minimum thickness 24 mm

- Timber to be properly seasoned, treated, and securely fixed to metal supports

Emergency / Exterior Staircase:

- Checkered aluminum plate, thickness 4 + 1 mm

- Panels to be anti-slip type and securely fixed to steel framing

All steel and metal profiles shall be cleaned, prepared and protected as follows:

Anti-rust primer: Two (2) coats

Final oil paint finish: Two (2) coats

Main Building entry stairs and cover and emergency entry ground floor:

Steel/metal profiles stairs structure, treads with aluminium checkered plate thickness 4+1mm. Steet structure for cover as well, covered with prepainted metal sheets and equipped with gutters.

Air-condition Split Unit DC Inverters:

Wall mounted

Power Supply: 220-240V, 1Ph, 50 Hz

Cooling/Heating Capacity 12000Btu/h

Energy Efficiency class: A++/A+

Refrigerant Type: R32

Remote control

Wall mounted

Power Supply: 220-240V, 1Ph, 50 Hz

Cooling/Heating Capacity 9000Btu/h

Energy Efficiency class: A++/A+

Refrigerant Type: R32

Remote control

#### Ablution Units:

The Contractor shall provide all necessary materials, labor, equipment, and supervision required for the complete execution of the ablution units in accordance with the project drawings and specifications. All works shall be carried out to achieve a durable, functional, hygienic, and aesthetically uniform installation.

Refer to table below provided as basis reference for works in ablution units.

Complete shower installations shall be provided and installed, including wall-mounted shower heads, flexible hoses, water taps, and all necessary accessories to ensure proper and reliable operation. Shower areas shall also be equipped with white PVC curtains fixed on stainless steel pipe holders.

Urinals shall be supplied and installed as wall-hung washout units complete with flushing rim, integral trap, and manual flusher system. Urinal partitions shall be installed between units and shall consist of waterproof compact panels with a thickness of 12 mm. These panels shall be impact-resistant, scratch-resistant, fully waterproof, finished in matte white, and sized at 100 x 40 cm.

Toilet and shower partitions, including doors, shall be constructed using 70 mm PVC profiles filled with 24 mm PVC sandwich panels. These partitions shall be fully waterproof, durable, and suitable for intensive use, ensuring adequate privacy and resistance to moisture.

Wash basins shall be provided and installed complete with hot and cold water faucets, rear overflow openings, and integrated pedestals made from the same material as the basin to conceal traps and pipe connections. Mirrors with dimensions of 60 x 40 cm shall be mounted above each wash basin, properly aligned and securely fixed.

Water closets shall be installed as complete units with dual-function flushing tanks and integrated bidet tubes. All toilet units shall be white and supplied with all necessary fittings and accessories for proper installation and operation.

Minimum of two floor drains per ablution unit, in addition to dedicated shower drains. All drains shall be fitted with stainless steel covers and have a 50 mm diameter outlet, properly connected to the network with adequate slope to ensure efficient water flow.

A 300-liter boiler shall be supplied and installed, fully connected to the water supply network. The boiler installation shall include all required fittings, valves, and accessories to ensure safe and efficient operation.

All materials used in the works shall be new, of approved quality, and suitable for wet and high-use environments. Workmanship shall comply with recognized industry standards and manufacturer recommendations. All finishes shall be properly aligned, free of defects, and executed to a high standard. The Contractor shall ensure that the entire installation is watertight, fully functional, and ready for use upon completion.

#### Roof cover

Two slopes roof is to cover the building structures for which designs are to be presented for approval prior to manufacturing and installation.

Roof to consist of roof steel trusses, with distance between trusses 244cm.

Roof covering is to be done using trapezoid pre painted corrugated metal sheet, with drip stop layer, 0.50mm thick, TR 40/240, color RAL 9002,  including roofing ridge cap and snow guards, flashings.

Roof delivered with horizontal and vertical gutters installed.

Horizontal gutters 150mm, made of pre painted metal sheet 0.6mm thickness. Color RAL 9002.

Rainwater down pipes, 100mm diameter, made of pre painted metal sheet 0.6mm thickness. Color RAL 9002.

All parts (union brackets, running outlets, stopend internal, pipe clips, offset bend, etc) are to be of the same material as the gutters and downpipes.

Roof eaves (soffit) are to be covered with 0.50mm “Piano” pre painted galvanized metal sheets.

Roof gables (A sides) are to be covered with 0.50mm “Piano” pre painted galvanized metal sheets. On both A sides ventilation grills are to be installed.

The roof fascia is to be covered with flat pre painted metal sheet 0.50mm thick. All the flashings are to be done using flat pre painted metal sheet 0.50mm thickness.

All materials and manpower for the works is to be provided by contractor.

#### Facade works

Facade works:

Although the office container is constructed with wall panels of 5 cm thickness, additional thermal insulation was foreseen as required to achieve acceptable energy efficiency and indoor comfort.

Container wall panels typically have limited thermal resistance due to their composite or metal-based structure, leading to higher heat losses and gains through the building envelope.

In order to reduce heat loss in winter and heat gain in summer, lower heating and cooling demand and meet energy efficiency targets lightweight façade is to be installed over facade perimeter walls/over the container panels/columns/beams, creating a uniform flat wall structure.

The facade shall be of expanded polystyrene boards 100mm thick over the panels and 50mm over the container columns/beams, with all necessary elements and layers including render finish and final paint, as per technical specification according to DIN EN 13501, and as per drawing provided.

- Before fixing the wall insulation system/polystyrene with adhesive (and fixings), it is required to check that the substrate is ready for bonding. The substrate should be pre-treated; brushed/swept making it free of any dust and dirt, any items obstructing the installation should be dismantled as well, for later reinstallation as required (rainwater down pipes, ect).

- The installation of polystyrene boards is to be done with adhesive mortar over the panels, and additional with mechanical anchor fixing as back up due to the existing substrate structure (panels).

Starter track is to be installed at the lowest point of the polystyrene boards.

Connections with other building units such as windows, doors, roof and place where the building units break through, as well as connections with building units made of glass, metal and wood must be sealed in.

Depending on the area, the sealing zone must be made rainproof by using render beads, joint sealing strips of the appropriate size or sealant.

- Basecoat with reinforcement mesh is to be applied over the polystyrene boards, with topcoat primer and decorative render finish.

- 30mm thick polystyrene plates according to DIN EN 13164 are to be used, bonded to the foundation wall.

- Lower part is to be plastered with decorative weather resistant coating, natural granulate product, while the upper part of the facade if to be painted with facade paint, color to be chosen by EULEX Representative on site.

Note: scaffoldings or other equipments (stairs/etc) are to be provided and installed by contractor for all the facade works including screen to secure particles/dust from spreading outside the working area.

As part of tender dossier, detailed designs of one container block ( Block 1,2,3 which are identical) has been provided which is to be used as a sample for design of other similar blocks.

Provided with set of drawings are also preliminary floor plans of all other blocks for which detail designs are to be part of design phase.

The activities listed below (of Block 1) shall be used as the basis of reference for the calculation of quantities, design development, execution, and pricing of positions of works for Blocks 1, 2, 3, 4, 5, 6, 13, 15 and 17.

Since this project is to be carried out on a design and build basis, any item, work, or activity that is not listed does not mean it is excluded. If additional works or components are required for the building to function properly, be safe, meet regulations, or be fully completed, they may still be requested and must be provided, even if they are not specifically mentioned.

Foundation works:

Excavation works for strip foundations: Excavated material is to be stored aside for refilling, while the surplus material is to be taken out from the compound to the Municipal designated dump site.

Provision of material, filling and compaction of strip foundations with gravel 0-31mm, thickness 10cm.

Backfilling around the foundations and removal of surplus material from site.

Provision of materials and installation of reinforcement as per structural foundation designs to be developed.

Provision of material and concreting of the reinforced strip foundation with concrete C-25/30, including formwork as required.

Grounding protection using FeZN strips throughout the perimeter with Zn rods embedded in the ground, as per final designs to be developed.

Construction Installation works:

Placement of containers steel structures in concrete strip foundation as per floor plans. All the structures will be transported on site by EULEX and contractor is to maneuver and position them within the Compound.

Dismantling of the ceiling panels from containers, removing debris out of site to a designated dump site.

Provide and install wall polyurethane sandwich panels t=50mm in container metal structures as per buildings floor plans.

Provision and installation of t=100mm polyurethane sandwich ceiling panels in the existing metal structure of the container. The panels must be well sealed with silicone sealant from the top so that the ceiling is completely waterproof.

Provide material and cover the top joints of wall-ceiling perimeter with pre-painted flat metal sheet (skirtings) thickness 0.55mm. Dim. (100+30+5) mm

Provide material and cover wall-wall corner joints with pre-painted L skirting thickness 0.55mm. Dim. (55+55) mm

Provide and install 100 mm of mineral wool insulation throughout the floor (office containers both floors), ablution units floor of the 1st floor and corridor ceiling of the first floor.

Provide material and install plastic sheet of 0.2mm all over the office floorings on both floors, ablution floorings and corridor ceiling of the first floor.

Provide material and install 20mm thick plywood flooring throughout the office containers and first floor corridor surface.

Provide and install 20mm thick water-resistant plywood flooring for the ablution units on the first floor.

Provide material and lay the final homogeneous layer of flexible PVC, through the floor of the office containers t=2 mm, including the floor of the ablution units on the first floor where the PVC should be 15 cm raised on the walls. PVC is to be welded & glued with proper adhesive. Skirting all around the perimeter of the surface is to be included in the price. Color to be chosen by EULEX Representative. PVC 2.0mm thick, commercial use, EN 649, classification as per EN 685, min. Class 33, areas with heavy traffic.

Provide and install galvanized metal sheet strips 41cm wide t=2mm for covering the floor joints of double office containers. Gaps between containers prior to being covered are to be filled with compressed insulation.

Provide, spread and compact gravel 0-30 on the Ground Floor (G.F) corridor & Ablution Units.

Provide and install floor thermal insulation styrodur, 25 kg/m3 in thickness of 120 mm (2x60mm), throughout the ground floor corridor over the gravel.

Provide material and construct reinforced concrete slab with flat uniformed finishing on the Ground Floor (G.F) corridor & Ablution Units included. Thickness of slab 100mm C20/25, reinforcement with steel mesh Q335, 8x8mm, division 150x150mm.

Provide material and lay the concrete screed th=4mm on the Ground Floor (G.F) corridor & Ablution Units

Provide material and construct entry staircase and cover, including stairs from emergency exit of the ground floor as required depending on the levels.

Provide material and construct first floor (F.F.) corridor structure consisting of iron rectangular profiles 60x40x3mm each 60cm (center to center) crosswise, and 40x2.6mm lengthwise, including L profiles 50x4mm lengthwise on both sides of the corridor and 100x60x4mm in front of staircase. The whole structure elements/profiles are to be made rust free, painted with antirust paint 2x.

Provide material and construct support structure above interior staircase, consisting of iron rectangular profiles 100x60x4mm, including L profiles 50x4mm lengthwise on both sides of the staircase. The whole structure elements/profiles are to be made rust free, painted with antirust paint 2x.

Provide material and construct complete interior staircase.

Provide material and construct exterior staircase for emergency exit.

Provide material and install laminate flooring for the GF and FF corridors suitable for commercial use, resistant to scratches and water, with 5mm sponge under layer, th =8mm. Include appropriate skirting profiles throughout the building and also aluminum skirting at the office entrance/building entrance.

Provide material and seal the joints between containers for double container rooms (walls/ceiling). Sealing is to be done with pre-painted flat metal sheet thickness 0.55mm, wide ~50cm. Prior to installation the gaps between two containers are to be filled with foam/mineral wool as required. Color similar to interior paint.

Provide and install the wooden timbers section 80 X50 mm every 60cm on the ceiling above the first-floor corridor.

Provide and install mineral fiber suspended ceiling, panels dim 600x600 mm, first class quality, complete with all the necessary fixtures/supporters for the ground floor and first floor ceiling above the corridors. Sample to be provided for approval prior to installation.

Provide material and paint the container structure in the corridor walls of GF and FF with acrylic enamel paint 2x. Paint characteristics: semi-gloss coating, eco-friendly, thinning with water. All equipment, windows, etc., are to be properly protected prior painting. Paint should be washable.

Supply and install 12000 BTU Split Unit Air Conditioner/ Inverter. Power Supply: 220-240V, 1Ph, 50 Hz Cooling/Heating Capacity 12000BTU/h Energy Efficiency class: A++/A+ Refrigerant Type: R32 Remote control Note: due to the facade to be installed over the container panels the brackets to be provided for the outside unit are to be longer.

Supply and install 9000 BTU Split Unit Air Conditioner/Inverter. Power Supply: 220-240V, 1Ph, 50 Hz Cooling/Heating Capacity 12000BTU/h Energy Efficiency class: A++/A+ Refrigerant Type: R32 Remote control Note: due to the facade to be installed over the container panels the brackets to be provided for the outside unit are to be longer.

Provide and install the office PVC entry doors. Doors are equipped with cylinder lock, and a minimum of three keys. Dim 95/210 cm. in advance, the wall panel must be cut according to the door dimensions.

Provide and install the Ablution PVC entry doors. Doors are equipped with cylinder lock, and a minimum of three keys. Dim 85/210 cm. In advance, the panel must be cut according to the door dimensions.

Provide and install Office PVC Window dim 95x125cm. Glass: double, fully insulated, thermal protection, 4+16+4mm, U≤1.4 W/m²K, in advance the panel must be cut according to the window size. Tilt and turn opening, Window is to be equipped with mosquito net on an independent frame with mechanism for opening and closing as needed.

Provide and install venetian blinds for building windows.

Provide and install vertical blinds.

Provide and install Ablution PVC Window dim 60x80cm, with thermal double glass 4+16+4mm, In advance the panel must be cut according to the window size. Tilt and turn opening, Window is to be equipped with mosquito net on an independent frame with mechanism for opening and closing as needed.

Provide and install main PVC entry double wing doors. The main entrance door should be of PVC profiles, dim 180/240cm.Glass: double, fully insulated, thermal protection, 4+16+4mm. Door is to be equipped with door lock complete, minimum three keys and hydraulic doors closure. U≤1.4 W/m²K

Provide and install PVC emergency door with window and fixed parts for closure of corridor east side in G.Floor and F.Floor. . -Glass: double, fully insulated, thermal protection, 4+16+4mm. -Door is to be equipped with anti-panic push bar, pneumatic door closer and possibility to close with a key from outside Dim. 180 x 240cm

Provide and install PVC window with fixed parts for closure of corridor side in the First Floor as per design provided. Glass: double, fully insulated, thermal protection, 4+16+4mm. Dim:180 x 240cm

Provide and install PVC window with fixed parts for closure of staircase, south facade for both floors as per design provided. Glass: double, fully insulated, thermal protection, 4+16+4mm. Dim:244 x 499cm

Ablution Unit works:

Provide with material and build the strip with siporex blocks to separate the shower area. Strip cross section 7.5x12cm.

Provide and install hydro-isolation of flooring with two component liquid hydro isolation in two coats. Also apply two coats of isolation 12 cm high in the perimeter walls.

Provide and install non slippery ceramic tiles R10 for toilets over the concrete screed.

Provide and install ceramic tile skirting, 12 cm in height, along the entire perimeter wall. The same ceramic tiles and joint material as the flooring is to be used, to ensure a uniform finish.

Provide with material and cover with ceramic tile the strip of siporex blocks in all 3 sides, including proper angle skirtings. The same ceramic tiles and joint material as the flooring is to be used, to ensure a uniform finish.

Provide and install complete set of shower heads and flexible hoses (wall hung as well), with water tap and other accessories for proper operation.

Provide and install urinals partitions. Partitions are to be of waterproof compacted panels with thickness -12mm, impact and scratch resistant, waterproof, color white, finish – mat. Dim 100x40cm

Provide and install shower partitions and toilet partitions with doors. Partitions and doors are to be of PVC Profiles 70mm filled with PVC sandwich panels t-24mm

Supply and install the PVC curtains white color with stainless steel pipe holder for showers.

Provide and install wash basin complete with faucet for cold and hot water, with rear overflow holes with integrated pedestal (same material as basin) to conceal the trap and connections.

Provide and install urinals complete with faucets. Urinals shall be wall-hung washout urinal, flushing rim, integral trap and shall be provided complete with manual flusher .

Provide and install toilet seats complete with flushing tank and built-in bidet tube. All water closets for toilets as shown on the drawings shall be dual function flush tank with built-in bidet tube, white, with complete fittings and mounting accessories

Provide and install mirrors over each washbasin, dim 60/40cm

Provide and install new floor drain (2 in each ab.Unit) and showers drain with stainless steel cover with 50mm OD outlet

Provide and install boiler 300ltr with conection to the water network.

#### Roof Cover

Provide materials, manufacture and install roof structure consisting of steel trusses, purlins. All the elements are to be made rust free, painted with antirust paint 2x. Roof structure design to be presented for approval prior to manufacturing.

Provide and install pre-painted corrugated metal sheet of t=0.55mm as roof cover, Price to include snow guards & ridge. Roof Cover needs to have drip stop layer (Anti-condensate Felt). Color RAL 9002.

Provide and place 100mm of mineral wool over the first-floor containers roofing ( between metal trusses) all over the surface.

Provide and install pre-painted metal sheet (piano) roof eaves, of 0.50mm thickness. Color RAL 9002 (fascia and soffit all sides).

Provide and install half round horizontal rain gutters 120mm, from pre-painted metal sheet 0.6mm thickness. Color RAL9002. Price shall include as well provision and installation of hangers and all the required accessories.

Provide and install vertical gutters (Rainwater down pipes), of pre-painted metal sheet 0.6mm thickness. Color RAL 9002.

Provide and install pre-painted metal sheet roof edges/A sides 0.50mm thickness (piano). Color RAL 9002.

Provide and install aluminum grills for under-roof ventilation, two on both A sides of the roof.

Facade Works

Provide materials and install lightweight facade made of expanded polystyrene plates 100mm thick ( over panels 80%) and 50mm(over columns 20%), with all necessary elements and layers including render finish and final paint, as per technical specification according to DIN EN 13501, the scaffoldings with screen to secure particles/dust from spreading outside the working area to be included in the price.

Provide materials and install perimeter insulation of the foundation wall, approximately 16 cm, by using 30 mm thick extruded polystyrene plates (styrodur) according to DIN EN 13164, including acrylic render finish 2.0 mm corn, high resistance to mechanical stress, high elasticity, good water vapor permeability, highly weather resistant

Provide and install window sill/ledge.

#### Electrical works

Refer to 4.4 Specifications below for all Electrical Installations

#### Heating works

Refer to point 4.5 Mechanical Installations

#### CIS works

Refer to point 4.7 CIS Installations

#### Fire Alarm System

Refer to point 4.8 Fire Alarm System specifications

### MSO Office Block # 12:

MSO Block is also a container block, but it differs from other typical blocks in the following points:

#### Foundation: refer to point 4.2.2.1

#### Construction Installation works:

For this block, second-hand office containers (8) shall be provided, but in this case, they will be fully equipped with internal wall and ceiling panels, windows, and doors, enabling the container block to be assembled and installed in accordance with the approved layout drawings.

Only minor interchangeable modifications are to be required to adapt the containers to the new design layout, as necessary to ensure proper fit and compliance with the approved drawings.

4 additional office PVC windows were requested to be installed by Security and those will be provided by EULEX but installed by contractor after cutting the wall panels.  T skirting is to be provided and installed around the panel/window after installation.

- PVC Toilet Window:

A PVC Framed window, tilt-and-turn opening, glazed with double glass 4+16+4mm. U≤1.4 W/m²K is to be provided and installed for in the container which is to be used as ablution.

The joint line between window and wall is to be covered with PVC or white aluminum color skirting ┴ profile from the inside.   Dim: 60x80cm

Window is to be equipped with mosquito net on an independent frame with mechanism for opening and closing as needed.

As office container is to be used for ablution the panel with office window is removed replaced with full panel where the window is to be installed.

- Main Entry Doors, emergency exit and corridor closure frame.

They are to be exterior PVC Framed Doors/closure frame. Contractor is to provide and install, including any skirting or elements required for closure of the corridor on both sides.

Double glazed: 4+16+4mm glass. U≤1.4 W/m²K

Dim of Main entry door: 180x240xm

Dimension of closure frame with emergency door: 180x240cm

Emergency doors are equipped with emergency exit hardware/ panic push bar with possibility to lock with the key from outside and hydraulic door closure.

Corridor flooring: Steel frame corridor structure with all the sublayers, Final cover: laminate Refer to point. 4.2.2.2 for detailed description of layers.

Roof: Refer to 4.2.2.4 for details.

All materials and manpower for implementation of the works are to be provided by contractor, apart from steel roof trusses which will be provided by EULEX (5EA).

Main Entry stairs and cover, ground floor emergency exit: Refer to 4.2.2.4.

Main Building entry stairs and cover and emergency entry:

Steel/metal profiles stairs structure, treads with aluminium checkered plate thickness 4+1mm. Steet structure for entry cover as well, covered with prepainted metal sheets and equipped with gutters.

Air-condition Split Unit DC Inverters:

Wall mounted

Power Supply: 220-240V, 1Ph, 50 Hz

Cooling/Heating Capacity 12000Btu/h

Energy Efficiency class: A++/A+

Refrigerant Type: R32

Remote control

Wall mounted

Power Supply: 220-240V, 1Ph, 50 Hz

Cooling/Heating Capacity 9000Btu/h

Energy Efficiency class: A++/A+

Refrigerant Type: R32

Remote control

Ablution Unit: One of the office containers provided is to be converted into ablution unit, therefore floor plywood is to be dismantled and replaced with waterproof plywood and new PVC layer 15cm raised to the wall.

For other specs refer to: 4.2.2.3

#### Electrical works

Provided containers are equipped with electrical installations (sockets, switches, lights). Contractor is to provide and modify the power supply in ablution unit only.

Electrical panel for this block will be provided as well. All other electrical installations are to be provided and installed by contractor.

Refer to 4.4 Specifications below for all Electrical Installations

#### Heating works

Refer to point 4.5 Mechanical Installations

#### CIS works

Refer to point 4.7 CIS Installations

#### Fire Alarm System

Refer to point 4.8 Fire Alarm System specifications

### Infirmary Block #14:

Infirmary Block consists of 8 new containers and 2 new ablution units connected with a corridor in between and covered with a two-slope roof.

#### Foundation:

Refer to point 4.2.2.1

#### Construction Installation works:

New office containers and ablution units are to be provided for the project as per specifications below and positioned over reinforced strip foundations.

Office Container 20ft, specifications:

Length: 605 to 606cm (depending on manufacturer the dimensions varies in mm)

Width: 243 to 244cm

External height: 259 to 262cm

Structure:

Mountable steel construction: top and base frame made of cold formed profiles of quality steel, corner pillars made of cold formed profiles, frames connected to corner pillars with bolts.

Design Loadings:

-   Wind loading of minimum 100 km/h without additional anchoring

-   A superimposed snow loading of min 100 kg/m2.

-   Floor permitted loading: min 2.00 KN/m2

- Static calculations of the container steel structure are to include/ensure future possibility of using the container in two story building (1+1).

Construction (frames and pillars): grease-removed, sand-blasted, zinc coated - wet (hot) treatment to European Standards, covered with 2 pack epoxy modified top coat or acrylic modified polyvinyl top coat, colour white (RAL 9001 or RAL 9002) .

Corner up-rights are insulated through mineral wool strips in order to prevent

"Thermal bridges".

The assembled container must be solid enough to enable transport and handling by any ISO means: crane, forklift, etc. Containers must be equipped with forklift pockets.

Walls:

PU (polyurethane) sandwich panels, fully interchangeable on both sides completed with dust and water proofing rubber seals.

Wall total thickness minimum 60mm.

External side plane sheet thickness: 0,5 mm. (pre painted)

Internal side plane sheet thickness: 0, 5 mm. (pre painted)

Ceiling/roof:

Slightly convex to allow drainage and stacking of containers. Rainwater to be drained through gutters inside roof edges.

PU Panel thickness 50 + 40mm rib.

• Outer steel sheet thickness: 0, 5 mm. (pre painted)

• Inner steel sheet thickness: 0, 5 mm. (pre painted)

Floor:

External: galvanised steel sheet metal in a thickness of min 0.5 mm,

Insulation filling: mineral wool among steel transverse supports, including steam blockage/PE foil

Plywood of minimum thickness of 18mm

Wall-to-wall flat linoleum/PVC cover glued to the panel. All joints PVC welded.

Permitted loading: min 2.00 KN/m2

Doors and windows:

The door is fitted into the wall panel, single fold door.

Aluminium or PVC external door.

Min width=90cm, minimum height 205cm.

Equipped with: no. 3 hinges adjustable in height, heavy plastic opening

(Internal and external) handles, a lock (with no. 3 keys), dust and water-proofing

gaskets.

PVC/Aluminium Window: fitted into the wall panel minimum width 80cm, minimum height 120cm with roller blinds. White in color. Double glazed.

Electrical Installations:

The electrical installation shall be designed in accordance with European Standards.

Equipped with electrical and grounding system to meet the requirements of electrical, cooling, heating, lighting of the office container.

Operating voltage 220/380V, 3Ph+N+G, 50 Hz,

External connection point: IP 54 protection rate

Internal PVC panel board equipped with:

- general thermo-magnetic differential switch: 40A

- 3X thermo-magnetic switch 16A

- 1X thermo-magnetic switch 10A

- 1X spare way

Outlets/sockets: 3 EA

Lights:  2 ceiling units, LED Panels and the switch.

All cabling is to be covered in PVC pipes.

The metal structure of the container to be ready to be connected to the grounding.

Containers to be connected in-between with clamps provided by contractor, specially designed for containers connection.

Ablution Units Specifications:

New ablution unit, outer dimension: 244x254cm (+-1cm)

Same construction as the Office Container.

Differences:

Windows: Size minimum 700mm x 500mm, opening in horizontal axis, or 60x80cm tilt and turn.

Floor: Wall-to-wall flat linoleum cover: 2mm thick glued to the chipboard panel and pulled up min 100mm on the side walls. All joints PVC welded. Colour: light grey. Waterproof plywood/board under PVC layer .

Electrical Installations: Damp-proof installation in accordance to the European Standards.

Electrical Fittings: Main distribution box with plastic cover.

Surface-mounted double sockets 220 V

Surface-mounted switches

Slim LED lights

Toilet Installations:

Distribution of sanitary water: poly-propylene pipes 1/2” and 3/4”, surface-mounted.

Sewerage pipe: PVC pipes, diameters 50 mm and 110 mm, surface-mounted

Container connections on facade wall; PVC pipe, diameter 110 mm, galvanised pipe 3/4”.

SANITARY EQUIPMENT:

-ceramic toilet pan with a PVC toilet cover, low mounted flush tank of 9 l capacity.

-ceramic urinal, with push button flush valve and an outlet siphon

-ceramic washbasin, with an outlet siphon, mirror (600x400mm).

Shower basis 90x90

Ventilation:

Air circulation must be provided through electric extractor fan with 15-18 air changes/hour and with speed control switch.

In each medical room there shall be a ceramic washbasin installed as well (3EA)

Corridor steel structure with sublayers – final layer laminate: Refer to point 4.2.2

Roof: refer to point 4.2.2

AC/Inverter: refer to 4.2.2 and numbers indicated in BOQ and preliminary dwg.

Entry stairs/cover and emergency exit: refer to 4.2.1 (same as other blocks).

Main Entry door and emergency exit door/panel: Refer to 4.2.2 and preliminary dwg

Aluminium sliding door:  is to be provided and installed for the emergency room, with clear opening of 110cm. Full panel no glass. At the position specified as per preliminary designs.

Ramp: An external access ramp serving the infirmary building.

A steel-structure access ramp with a maximum gradient of 6–8.5%, in compliance with accessibility requirements. The ramp surface shall be finished with non-slip checkered aluminum plate (minimum 4+1 mm thickness). All steel components shall be treated and painted for corrosion protection and final paint white 2x. Include continuous handrails at 90cm  heights for user safety.

#### Electrical works

Containers and ablution units will come equipped with panels and all installations. Contractor to provide and install all other installations for the building including electrical panel.

Refer to 4.4 Specifications below for all Electrical Installations

#### Heating works

Refer to point 4.5 Mechanical Installations

#### CIS works

Refer to point 4.7 CIS Installations

#### Fire Alarm System

Refer to point 4.8 Fire Alarm System specifications

### Storage Block # 7:

Storage Block #07 consists of Sea Containers (7EA) with dimensions 605x244cm which are to be provided on site by EULEX:

#### Foundation:

Refer to point 4.2.2.1

#### Construction/Installation works:

Sea Containers provided by EULEX are to be positioned by contractor over strip foundations as per preliminary layout provided.

The provided Sea Containers are second-hand units; therefore, the external surfaces/facade shall be thoroughly cleaned and prepared, followed by the application of two coats of metal primer and two coats of oil-based paint suitable for steel surfaces.

They are to be covered with two slope steel structure roof to be designed to fit the layout of the block.

Technical Specifications of materials and installation works for the roof as per point 4.2.2.

#### Electrical works

Only basic installation (lights +1 socket/switch/emergency light) for each container.

Refer to 4.4 Specifications below for all Electrical Installations

#### CIS works

Refer to point 4.7 CIS Installations

#### Fire Alarm System

Refer to point 4.8 Fire Alarm System specifications

### Cafeteria with kitchen appliances

The Contractor shall design and construct reinforced concrete strip foundations suitable for the site soil conditions in accordance with Eurocodes (EN 1992 and EN 1997).

Prior to construction, the Contractor shall verify the excavation levels.

Foundations shall generally consist of C25/30 reinforced concrete cast.

The dimensions and reinforcement shall be determined by structural calculations. Excavation, compaction of formation level, proper concreting, vibration, and curing are all the responsibility of the Contractor.

Anchor bolts for the steel structure shall be cast into the foundations in accordance with approved final drawings.

Construction (Structure):

The building shall be of a steel frame structure designed and executed in accordance with EN 1993 and EN 1090 standards. The system shall consist of steel square and rectangular columns, beams, and bracing elements ensuring overall stability. Steel elements shall be fabricated from structural steel grade S235 or higher, properly prepared by sandblasting (SA 2½) and protected with anti-corrosion coatings.

All structural connections, base plates, and bracing systems shall be designed by the Contractor and submitted for approval. The complete structure must ensure safety, durability, and resistance to wind and operational loads.

Walls and Floor:

External walls shall be constructed using profiled pre painted steel sheets fixed to the steel structure, with internal lining of gypsum boards installed on metal studs. Thermal insulation of minimum 100 mm mineral wool shall be provided within the wall cavity, along with a vapor barrier layer to prevent condensation.

Internal partition walls shall consist of lightweight metal stud systems with 2 x gypsum boards on both sides and insulation infill required (W112).

The floor shall be constructed on a compacted granular sub-base with integrated service installations. A reinforced concrete slab shall be provided above a damp proof membrane and thermal insulation layer with 4-5cm screed/leveling layer on top. In wet areas such as kitchens and toilets, appropriate slopes toward drainage points shall be ensured and waterproofing shall be applied to floors and lower wall sections. Floor finishes shall consist of non-slip ceramic tiles suitable for the intended use, while wall finishes shall include painting in dry areas or ceramic tiling in wet areas (kitchen, toilet, service area).

## Roof and Ceiling

The roof structure shall consist of steel trusses designed by the Contractor, supported by purlins and bracing elements to ensure stability. Roof covering shall be made of corrugated pre-painted steel sheets incorporating an anti-condensation layer.

Thermal insulation, consisting of mineral wool of adequate thickness, shall be installed along with a vapor barrier to ensure proper thermal performance.

The internal ceiling shall be constructed as a suspended ceiling system using mineral fiber panels supported on a metal grid.

Rainwater drainage shall be ensured through a system of gutters and downpipes made of pre painted metal sheets.

Windows and Doors

Windows and doors shall be constructed from PVC profiles with thermal insulation properties in accordance with applicable standards. Glazing shall be double-glazed units (4+16+4 mm) U-value of 1.4 W/m²K. All units shall be weather-tight, durable, and suitable for frequent use. Opening mechanisms, dimensions, and accessories shall be as per approved design drawings. The Contractor shall submit technical datasheets for approval prior to installation.

Sanitary

The Contractor shall supply and install all sanitary fixtures as indicated in the design drawings. Toilet units shall be of the dual-function type, incorporating a flush tank and integrated bidet system, finished in white and complete with all necessary fittings, connections, and mounting accessories.

Washbasins, including both single and double units, shall be wall-hung type with rear overflow and integrated faucet ledge. Each unit shall be supplied complete with chrome-finished faucets, hot and cold water connections, traps, and all standard accessories required for proper operation.

Urinals shall be wall-hung washout type with flushing rim and integral trap, complete with manual flushing mechanism and all associated fittings.

All lavatory faucets shall be manual-operated, finished in chrome, and designed for durability, hygiene, and ease of maintenance. All sanitary installations shall comply with relevant plumbing standards and be coordinated with the overall building design.

Air Conditioning:

The system shall include three split-type air conditioning units / Invertor of 18,000 BTU capacity each. Installation shall include all necessary drilling, piping, electrical connections, supports, and accessories.

Containerised Freezer and Reefer Cold Rooms:

- Freezer Container (605x244cm) is to be provided by EULEX while installed by Contractor as part of the building, as per preliminary designs.

- Reefer Cold chambers –vegetables and diary:  with individual cooling and control of temperatures/command box.

The Contractor shall supply and install compact modular refrigerated container as per preliminary design provided.  Units shall be constructed with insulated PU/PIR sandwich panels ensuring airtight and hygienic conditions (244x605cm).

The corridor is to be in ambient temperature.

Each unit/chamber shall be equipped with an independent refrigeration system capable of maintaining temperatures in the range of  +2 / +4  with digital control and uniform air distribution. Insulated door with sealing gasket - minimum dimension 90x200cm.

Internal surfaces shall be smooth, washable, and suitable for food storage.

Fruits and vegetables: +2°C to +4°C

Dairy products: +2°C to +4°C

The Contractor shall complete installation, testing, and commissioning, ensuring full operational performance.

Kitchen Appliances:

Kitchen appliances as per BoQ # 15 and specifications are to be provided and installed by contractor.

#### Electrical works

Refer to 4.4 Specifications below for all Electrical Installations

Refer to list of kitchen appliance to be provided and preliminary designs for electrical connections required for kitchen island and other.

#### HVAC works

Refer to point 4.5 Mechanical Installations

#### CIS works

Refer to point 4.7 CIS Installations

#### Fire Alarm System

Refer to point 4.8 Fire Alarm System specifications

Pergola cover for the terrace:

Pergola cover is to be provided and installed for the terrace, area to be cover is marked in the drawing.

Fabric of pergola must be resistant in whether conditions, sun, rain, wind and snow according to EU standards and regulation, with UV protection, with protective layer consisting of polymers in liquid or solid form or similar, to be easily folded during closure and to open easily.

The structure of Pergola is to be with aluminum profiles according to DIN EN 573-3 standards. The structure must have the build in horizontal and vertical gutters for removal of water outside the terrace. Color of structure will be assigned by Project Manager.

Motor is to have capability to smoothly open and close the fabric of pergola and to have certificate of origin from producer.

Pergola is to have integrated led lighting system.

The pergola is to be open / closed electronically with remote controls but also is to have the capability to be open / close manually.

### Gym Building & Outdoor activities areas

The Gym building shall be designed and constructed as a modular steel structure building using insulated sandwich panel systems, based on the initial concept drawings provided.

The Contractor shall be fully responsible for developing the detailed design, including architectural, structural, and installation solutions, in accordance with the operational requirements of the facility based on conceptual design/floor plan provided with.

Prior to design development, the Contractor shall carry out site investigations and surveys to verify all existing conditions. Based on these findings, the Contractor shall perform all necessary engineering calculations and prepare complete working drawings and details for approval. All dimensions and levels shall be verified on site before fabrication, and no manufacturing shall commence prior to approval of drawings, materials, and samples by the Contracting Authority.

The majority of fabrication works shall be carried out off-site in the Contractor’s workshop to ensure quality and minimize site activities, with on-site works primarily limited to assembly and installation.

Steel Structure

The building shall consist of a steel frame structure designed in accordance with Eurocode 3 (EN 1993) and executed in accordance with EN 1090. The structure shall ensure stability, durability, and resistance to all imposed loads.

Minimum clear internal height in the gym training area shall be 4.0 meters with no obstructions.

The structural system is to consist of IPE sections as primary members combined with secondary U profiles, or equivalent solutions, fully justified by structural calculations.

Steel material shall be minimum grade S235JR in accordance with EN 10025.

All steel elements shall be surface treated by sandblasting to grade SA 2½ in accordance with BS EN ISO 8501-1.

Protective coating shall consist of at least two layers of anti-corrosion primer applied in the workshop. Final finishing shall be completed with two coats of oil-based paint in the selected color ensuring a uniform appearance.

Connections shall be bolted to allow dismantling when required. Any welding carried out on site shall be treated and protected with equivalent anti-corrosion coating.

Wall Panels

External walls shall be constructed using prefabricated sandwich panels with polyurethane insulation core. Panels shall have an external and internal facing of pre-painted galvanized steel sheets with minimum thickness of 0.5 mm and color RAL 9002.

Panel thickness shall be of 100 mm.

Installation shall follow manufacturer specifications. A detailed panel layout and fixing plan, including type and spacing of fasteners, shall be submitted for approval prior to installation. All external fasteners shall be corrosion resistant.

Roof Panels

The roof shall be constructed using insulated sandwich panels with polyurethane core installed over steel purlins. Panel thickness shall be minimum 100 mm. External face thickness shall be minimum 0.5 mm and internal face 0.4 mm, pre-painted in RAL 9002.

The roof system shall include ridge elements, closures, and sealing accessories to ensure full watertightness and resistance to weather conditions.

Panels shall comply with EN 14509.

A complete installation and fastening plan shall be submitted for approval prior to works. All exposed fasteners and accessories shall be corrosion resistant.

Flashings, Gutters and Rainwater System

All flashings, ridge caps, gutters, downpipes, fascia, and drainage components shall be made of pre-painted galvanized steel sheets in RAL 9002. The system shall be designed to safely collect and discharge rainwater and prevent water ingress into the building envelope.

All accessories such as brackets, outlets, joints, and fixing elements shall be of compatible material and corrosion resistant.

Doors

Main entrance doors shall be designed as durable, weather-resistant units compatible with the building envelope and approved design. Aluminium profiles.  Same with the sliding door as an exit to the outdoor Gym area.

Emergency exit doors shall be single and double leaf steel doors opening outwards in accordance with EN 1125.  Door leafs shall be constructed of galvanized steel sheets (minimum 1 mm thickness) filled with mineral wool insulation. Doors and frames shall be powder-coated in RAL 9002. Each door shall be equipped with panic hardware (push bar), door closer, and external opening capability with key and handle. A minimum of three keys shall be provided per door.

An aluminium sliding door system shall be installed providing access to the outdoor gym area, designed for durability, smooth operation, and weather resistance.

Windows:

Windows shall be constructed from aluminum profiles with thermal break properties, designed to ensure weather tightness and durability, suitable for sandwich panels installation system. Glazing shall consist of double-glazed units (minimum 4+16+4 mm) with a maximum U-value of 1.4 W/m²K.

Dimensions, opening types, and positioning shall be set with final approved design drawings. All window systems shall be supplied with full technical documentation prior to approval.

In conceptual design minimum dimensions of doors, windows have been indicated, the dimensions can slightly increase or change in form for facade aesthetics or due to structural solution once final designs are developed.

Interior Works and Finishes

Changing rooms/toilets/showers:

Internal finishes for changing rooms and toilet areas shall be designed to provide a durable, hygienic, moisture-resistant, and easy-to-maintain environment suitable for high-traffic gym facilities. All materials shall be fit for purpose, compatible with wet areas, and installed in accordance with manufacturer recommendations and relevant standards.

Walls shall be constructed using moisture-resistant gypsum board systems on metal framing.

Changing room paint finish: Washable, resistant to impact and strain.

Shower and toilets: Ceramic tiles – full height in showers and minimum 1.5 meters in toilets.

Floor changing rooms/showers: Non-slip floor tiles R11. Wear-resistant and heavy duty. Easy to clean and maintain.

Ceiling: Water resistant suspended ceiling boards.

Floor in Gym area: Interlocking Rubber Gym Mats (Final Wearing Surface) will be provided and installed by EULEX.

Contractor is to provide material and construct all required sublayers to provide watertight and insulated building floor structure with final layer being non-slip epoxy flooring system.

Sanitary Elements

Sanitary facilities shall be designed and equipped by the Contractor based on the building usage requirements and conceptual preliminary designs. This shall include toilets, washbasins, showers, and associated plumbing systems, ensuring hygienic, durable, and efficient operation.

All installations shall comply with applicable plumbing standards and be fully coordinated with architectural and structural layouts.

Saunas:

Sauna must NOT be built directly off steel structure or sandwich panels.
It must be constructed as a self-contained internal “box” with its own insulation, vapor control, and finishes. It must be like a standalone enclosure within the building.

The Contractor shall be fully responsible for:

Structural framing system, thermal and vapour control, internal finishes and benching, heating equipment and controls, ventilation, electrical and fire safety compliance.

All designs shall be coordinated with architectural, structural, and other project designs.

Main Entrance Cover

The main entrance shall be protected by a canopy or cover constructed from steel profiles and matching roofing materials. The structure shall be securely fixed, weather-resistant, and designed to provide effective protection against rain and environmental conditions while integrating with the overall building design.

Outdoor Gym and Basketball Half-Court

The Contractor shall design and execute the outdoor gym and associated basketball half-court area in accordance with the intended functional use.

For details of asphalted surfaces refer to ground /infrastructure works.

Contractor is to mark the field lines with two-component polyurethane paint and provide a complete basketball post system, including: Post / pole, backboard, rim and net, all brackets, fixings, and accessories.

It should be suitable for outdoor installation, corrosion-resistant and durable under weather exposure and impact loads.

Outdoor GYM: EULEX will provide the steel structure (existing on the old compound) contractor is to install it on the outdoor GYM area, see below existing structure design.

DWG of the outdoor GYM – provided by EULEX to be installed by contractor

#### Electrical works

Refer to 4.4 Specifications below for all Electrical Installations

#### Heating works

Refer to point 4.5 Mechanical Installations

#### CIS works

Refer to point 4.7 CIS Installations

#### Fire Alarm System

Refer to point 4.8 Fire Alarm System specifications

### Training House

Training House is to be a modular steel structure building with sandwich panels as per conceptual preliminary design provided, with specifications and requirements as set below.

The works shall be completed based on the final structural designs to be prepared by the Contractor.

Prior to the developing the designs further, the Contractor shall carry out site investigations/survey.

Based on the conclusions of the site surveys, the Contractor shall carry out engineering calculations and shall prepare the required working drawings/details.

Prior to commencing manufacturing all the measurements are to be confirmed on site.

No manufacturing works are to commence prior to approval of final drawings, lists, materials to be used by EULEX BMU Representative, and approval of samples.

After approval of the designs and materials most of the manufacturing works are to be carried out at the contractor’s fabrication workshop ahead, keeping the activities on site to minimum up to the assembling/construction period on site.

Steel Structure:

Refer to 4.2.7 – similar to GYM

Wall Panels:

Refer to 4.2.7 for external walls

Roof Panels:

Refer to 4.2.7 for roof sandwich panels

Flashings, gutters, rain downpipes, fascia:

All flashings, gutters, rain downpipes, eaves, fascia to be foreseen with the design for the overall storage building shall be of pre painted galvanized metal sheet, color RAL 9002.

Main Entry Door:

Main entrance doors shall be designed as durable, weather-resistant units compatible with the building envelope and approved design. Aluminium profiles.

Emergency Exit Door:

Door leafs: sheet thickness 1mm, filled with mineral wool for thermal insulation, full panel no glazing.

Surfaces: Door leaf and frame shall be galvanized and powder-coated with a primer in off-white (based on RAL 9002).

Equipped with emergency exit hardware (panic push bar) and door closure mechanism.

The door should have the possibility to open from outside with a key and handle.

Minimum 3 keys.

Extreme emergency, Outward-opening (EN 1125).

Single-leaf steel door, dim.900x2050mm.

Sliding Door to the Outdoor GYM area

Interior doors: Interior aluminum framed doors – full panel no glass.

Windows:

Windows shall be constructed from aluminum profiles with thermal break properties, designed to ensure weather tightness and durability. Glazing shall consist of double-glazed units (minimum 4+16+4 mm) with a maximum U-value of 1.4 W/m²K.

Dimensions, opening types, and positioning shall be in accordance with final approved design drawings. All window systems shall be supplied with full technical documentation prior to approval.

In conceptual design minimum dimensions of doors, windows have been indicated, the dimensions can slightly increase or change in form for facade aesthetics or due to structural solution once final designs are developed.

Interior work and finishes:

Interior partitions shall be of sandwich panels polyurethan filling, 50m thickness, fixed on steel supporting structure consisting of rectangular steel profiles 60x40x3mm.

Flooring:

Contractor is to provide material and construct all required sublayers to provide watertight and insulated building floor structure with final layer being non-slip epoxy flooring system.

Main Entrance Cover:

The main entrance shall be protected by a canopy or cover constructed from steel profiles and matching roofing materials. The structure shall be securely fixed, weather-resistant, and designed to provide effective protection against rain and environmental conditions while integrating with the overall building design.

#### Electrical works

Refer to 4.4 Specifications below for all Electrical Installations

#### Heating works

Refer to point 4.5 Mechanical Installations

#### CIS works

Refer to point 4.7 CIS Installations

#### Fire Alarm System

Refer to point 4.8 Fire Alarm System specifications

### Recreation Building

The Contractor shall design and construct reinforced concrete strip foundations suitable for the site soil conditions in accordance with Eurocodes (EN 1992 and EN 1997).

The dimensions and reinforcement shall be determined by structural calculations. Excavation, compaction of formation level, proper concreting, vibration, and curing are all the responsibility of the Contractor.

Anchor bolts for the steel structure shall be cast into the foundations in accordance with approved shop drawings.

Construction (Structure):

The building shall be of a steel frame structure designed and executed in accordance with EN 1993 and EN 1090 standards. The system shall consist of steel square and rectangular columns, beams, and bracing elements ensuring overall stability. Steel elements shall be fabricated from structural steel grade S235 or higher, properly prepared by sandblasting (SA 2½) and protected with anti-corrosion coatings.

All structural connections, base plates, and bracing systems shall be designed by the Contractor and submitted for approval. The complete structure must ensure safety, durability, and resistance to wind and operational loads.

Walls and Floor:

External walls shall be constructed using profiled pre painted steel sheets fixed to the steel structure, with internal lining of gypsum boards installed on metal studs. Thermal insulation of minimum 100 mm mineral wool shall be provided within the wall cavity, along with a vapor barrier layer to prevent condensation.

Internal partition walls shall consist of lightweight metal stud systems with 2 x gypsum boards on both sides and insulation infill required (W112).

The floor shall be constructed on a compacted granular sub-base with integrated service installations. A reinforced concrete slab shall be provided including a damp proof membrane and thermal insulation layer with 4-5cm screed/leveling layer on top. In wet areas such as kitchens and toilets, appropriate slopes toward drainage points shall be ensured and waterproofing shall be applied to floors and lower wall sections. Floor finishes shall consist of non-slip ceramic tiles suitable for the intended use, while wall finishes shall include painting in dry areas or ceramic tiling in wet areas (kitchenette, toilets area).

Roof and Ceiling

The roof structure shall consist of steel trusses designed by the Contractor, supported by purlins and bracing elements to ensure stability. Roof covering shall be made of corrugated pre-painted steel sheets incorporating an anti-condensation layer.

Thermal insulation, consisting of mineral wool of adequate thickness, shall be installed along with a vapor barrier to ensure proper thermal performance.

The internal ceiling shall be constructed as a suspended ceiling system using mineral fiber panels supported on a metal grid.

Rainwater drainage shall be ensured through a system of gutters and downpipes made of pre painted metal sheets.

Windows and Doors

Windows and doors shall be constructed from PVC profiles with thermal insulation properties in accordance with applicable standards. Glazing shall be double-glazed units (4+16+4 mm) U-value of 1.4 W/m²K. All units shall be weather-tight, durable, and suitable for frequent use. Opening mechanisms, dimensions, and accessories shall be as per approved design drawings. The Contractor shall submit technical datasheets for approval prior to installation.

In conceptual design minimum dimensions of doors, windows have been indicated, the dimensions can slightly increase or change in form for facade aesthetics or due to structural solution once final designs are developed.

Sanitary

The Contractor shall supply and install all sanitary fixtures as indicated in the design drawings. Toilet units shall be of the dual-function type, incorporating a flush tank and integrated bidet system, finished in white and complete with all necessary fittings, connections, and mounting accessories.

Washbasinsshall be wall-hung type with rear overflow and integrated faucet ledge. Each unit shall be supplied complete with chrome-finished faucets, hot and cold water connections, traps, and all standard accessories required for proper operation.

All lavatory faucets shall be manual-operated, finished in chrome, and designed for durability, hygiene, and ease of maintenance. All sanitary installations shall comply with relevant plumbing standards and be coordinated with the overall building design.

Air Conditioning:

The system shall include two split-type air conditioning units / Invertor of 12,000 BTU capacity each. Installation shall include all necessary drilling, piping, electrical connections, supports, and accessories.

Entrance/EXIT Stairs and Covers

The main entrance shall be protected by a canopy or cover constructed from painted steel profiles, complete with roofing materials matching or complementing the main building design. The canopy structure shall be securely anchored to the building or supporting elements, fully weather-resistant, and designed to provide effective protection against rain, sun exposure, and other environmental conditions.

The design shall ensure visual and architectural integration with the overall building appearance, including appropriate finishes and detailing.

Access to entrance shall be provided by a set of entry stairs. The stairs shall be constructed of durable, non-slip materials suitable for external use, with adequate width, riser, and tread dimensions in accordance with relevant standards. Handrails shall be included), and the entire assembly shall be structurally stable, safe, and resistant to weathering and corrosion.

Same applies also to the exit to the barbeque area.

#### Electrical works

Refer to 4.4 Specifications below for all Electrical Installations

#### Heating works

Refer to point 4.5 Mechanical Installations

#### CIS works

Refer to point 4.7 CIS Installations

#### Fire Alarm System

Refer to point 4.8 Fire Alarm System specifications

### MSD Building Refurbishment

#### MSD Workshops and stores ( Transport, Logistics and BMU)

MSD Building is an existing building on site consisting of combined structure reinforced concrete and metal structure. While columns and beams are of reinforced concrete skeleton the roof structure is of metal structure/trusses.

The building is to be modified to accommodate the needs of Mission Support Department consisting of Transport, Logistics and Building Management workshops, stores, and offices.

Existing condition layout and preliminary layout for the modifications are provided with the drawings set.

The building has been separated into two zones, offices with separate entrance to be opened at the south facade of the building and store/workshops with entrances on the east facade of the building.

Dismantling/demolishing works:

Prior to commencement of any works to be dismantled/demolished are:

- Raised platforms and stairs consisting of slab with hollow clay blocks and concrete walls, at a height of 1 to 1.2meters.

- Concrete staircase at the back offices corridor and access door.

- Front facade windows and main entry door where the new rolling doors will be positioned.

- Dismantling of some of the windows where offices will be created so they can be replaced with new windows with tilt and turn opening.

- Dismantling of electrical installations and panel, as are not up to standard.

- Dismantling and demolishing works of toilets and other.

All debris is to be removed from site to the designated authorised dump site.

As per preliminary designs provided openings are to be created for three rolling doors to come on the east facade providing access to Logistics, BMU and Transport workshops.

Industrial sectional rolling doors, two of dim 400x400+60cm and one of dim.320x400+60cm

The rolling door is to function automatically through a remote control & operator, with integrated open/stop/close operation, soft start and stop door travel, adjustable speed, but also possible to operate it manually from the inside.

The panel sections made of double-skinned galvanized steel, surface - coated RAL 9002, 42 mm thick PU-foamed.

The door is to comply with EN Standard 13241-1.

Track application shall fit precisely to the building.

Measurements to be taken on site.

There shall be pedestrian door integrated within as well.

Internal partitions:

Division between units’ space is to be done with polyurethane thermal insulation sandwich panels, 5cm thickness, for which a supporting structure with steel profiles 60x40x3mm is to be manufactured and installed fixed on the ground, roof steel structure and walls.

Outer and inner covering: profiled metal sheet 0.5mm (pre painted RAL 9002).

Walls and flooring are to be repaired after demolishing works of the platforms and stairs.  The final layer of the whole surface is epoxy flooring.

Floor:

Two components epoxy paint as a final layer, including epoxy flooring skirting 12cm high to the wall.

The floor surface is to be well prepared with shot blasting machine, cleaned and dust removed/vacuumed.

The surface is painted with primer and two layers of epoxy paint enriched with quartz.

New joints are to be cut and filled with elastic polyurethane joint filler.

There are two emergency doors to be installed for the building as indicated in preliminary designs equipped with push bars.

Metal solid door, equipped with emergency exit hardware (panic push bar) and door closure mechanism.

The door should have the possibility to open from outside with a key and handle. Minimum 3 keys.

Extreme emergency,

Outward opening (EN 1125).

Painting:

The interior of the Workshops and store (walls) shall be painted. Perimeter walls are made of concrete blocks, plastered, currently painted grey.

Up to the height of 140cm the wall surface shall be painted with oil paint 2 x, previously cleaning, scraping and repairing the surface as and where required.

The upper part of walls surface shall be treated with primer, prior to applying two coats of interior emulsion paint. Colors to be chosen by EULEX Representative.

Relocation of vehicle lifts:

There are three vehicle lifts currently within the old Vehicle Workshop located in Mitrovica Transport workshop (approximately 4km distance from the new workshop) which are to be dismantled.

- 2 post electro hydraulic lift, capacity 4000kg (2 EA)

- 4 post electro hydraulic lift, capacity 8000kg (1EA)

Dismantling of the lifts is to be done with due care, starting with disconnecting the power supply and other connections, paying attention also to all the tanks containing liquids used for machine operation.

The dismantling is done in reverse sequence to that followed for installation.

Contractor is to protect all the parts so that are not damaged during transportation and sort/mark accordingly for easier re-installation on site.

All parts are to be lifted, transported and reinstalled with due care as per manufacturer’s instructions.

Reinstallation in the new workshop will be done after the refurbishment works are finalized and all the required connection points are prepared for all 3 lifts.

Timing / schedule of relocation of lifts is to be mutually agreed between contractor, BMU and Transport Representatives, including final positioning of the lift within the new building prior to being anchored to the floor.

Sample picture of the 4 posts lift – 8000kg

The installation on site is to be done on the existing flooring.

The existing reinforced concrete slab is expected to support the lifts, if any issues during installation it will be reviwed at the time.

The lifts are to be connected to power supply and air line from compressor.

Sample picture of 2 posts lifts – 4000kg

Upon completion of the installation of lifts the same are to be controlled/inspected for operation as per manufactureres instructions and also for their safety.

EULEX will afterwards carry inspection  by specialised body as well certify them for use.

Vehicle Exhaust System

Capturing airborne particles at the source is the most effective method for removing exhaust emissions. The system is to be designed to remove hazardous exhaust emissions in the most effective way, thereby providing a healthier work environment.

The system is to exhaust fume straight from the vehicle exhaust pipes and is to be suitable for all types of vehicles.

The design shall take into account factors such as engine sizes, exhaust gas temperatures, method of connection to the vehicle to ensure a fully functional cost effective and suitable solution obtained.

Vehicle Exhaust Extraction System is to be foreseen with two units, as indicated in the preliminary layouts.

Extraction Units is to be easily operated, equipped with all the required accessories (complete extraction unit kit including but not limited to the fan/channel/hose reel/extraction hose/nozzle, etc).

In this arrangement the extraction hose is to be wound onto a drum.

Picture – as a sample

When not in use the hose must rewind onto the drum and stores off the floor thus reducing trip hazards.

Materials and Equipment installed: All CE marked according to the common technical and EU rules.

Upon Installation Transport Technicians shall be provided with all the required information on functionality of the units and trained as required for the usage of the same.

Air piping for Compressor:

EULEX will position compressor on the exterior of the building as indicated in dwg.

From which contractor is to provide materials and install galvanized steel pipes running inside fixed on the wall alongside the workshop distributing air to each equipment requiring it, including the lifts. 8-10 bars pressure.

Below is list of equipment to be positioned inside the workshop indicating the need for power supply and compressed air connection.

Also main equipments are positioned in the preliminary building layout provided.

The office space on the 1st floor and resting area is constructed using W112 partitions, a metal stud system with gypsum plasterboards on both sides and insulation in between. Joints are to be taped and finished to provide a smooth surface suitable for paint.

Flooring is specified as laminate with a commercial wear rating of AC4/AC5, installed over a moisture-resistant underlay.

The ceiling system is a suspended ceiling grid with 600x600 mm mineral fiber tiles.

On the ground floor, the layout incorporates shower and toilet units as indicated in the drawings, alongside reception rooms for both the Transport Workshop and Logistics Supply. Each reception room is designed with a direct entry door from the exterior, ensuring customer access without passing through the workshop or store facilities.

Since these reception areas were previously toilet units, after demolishing works, they require full wall plastering to restore surfaces, followed by painting.

In the toilet and shower areas, syporex partitions are to be constructed as per the provided drawings, ensuring proper separation of sanitary cubicles. The floor is to be covered with a cementitious screed, laid to a minimum thickness of 50mm.

Hydroinsulation is to be applied across toilet and shower floors and walls to ensure watertightness. Over this, floor tiles with anti-slip properties will be installed, while walls will be finished with ceramic wall tiles up to full height, ensuring durability and hygiene.

The toilets are to be fitted with toilet seats complete with water flush cisterns and integrated built-in bidet functionality. Urinal sets are to be provided and installed in accordance with the layout drawings, including concealed flush systems and appropriate drainage connections.

Each shower unit is to be equipped with a shower head and flexible hose, wall-mounted, together with a water tap and properly graded shower drainage to ensure efficient water removal.

Washbasins are to be installed complete with water taps, traps, and connections.

A hot water system is to be provided via 80-liter boiler, wall-mounted and connected to both cold water supply and electrical power, ensuring adequate hot water capacity for the sanitary facilities.

Each toilet and shower room is fitted with a wall mirror of minimum dimensions 600 x 800 mm, securely mounted and finished with polished edges or framed for safety.

A steel staircase is to be manufactured and installed for the Transport Workshop, designed in accordance with structural load requirements and fire safety standards, with anti-slip treads and protective railing.

#### Office Section within MSD Building

There shall be an office section created withing the MSD Building with main entry on the south facade of the building.

Openings for new doors and windows are to be created by cutting and demolishing the existing façade wall, constructed of 200 mm thick concrete blocks with insulation. Debris is to be removed from site and transported to an authorized dump facility. Over each new opening, reinforced concrete lintels are to be provided and installed to ensure structural stability.

A complete mid-floor system is to be supplied, manufactured, installed, anchored, and finished to create first-floor offices. This system includes all steel structural elements, sub-layers, finishes, fixings, and connections to the existing reinforced concrete building structure. Using the 6 meter floor-truss spacing, a two-story office arrangement is achieved.

The scope also includes a supporting structure for the suspended ceiling of the first floor.

An interior steel staircase is to be manufactured and installed for the administrative part of the building. Designed in accordance with structural load requirements, with anti-slip treads and protective railing.

For perimeter walls, galvanized steel stud frameworks are to be fixed to sandwich panels via brackets, with insulation in between and a single 12.5 mm plasterboard layer on the inside, prepared for painting.

Internal partitions are to be constructed as per the new layout using W112 plasterboard partitions. Comprising of metal stud frameworks with 2 x 12.5 mm plasterboards on both sides and mineral wool insulation in between, including reinforced framing at door openings. Moisture-resistant partitions (plasterboards) of the same type are specified for wet areas.

Ceilings are to be fitted with mineral fiber suspended ceiling panels, 600 x 600 mm, complete with fittings. Wet areas will use suspended ceiling panels suitable for humid conditions.

Floor finishes include laminate flooring in offices and corridor, ceramic floor tiles in toilets and kitchenette, and wall tiles in toilets and kitchenette.

For the new offices created there shall be exterior PVC windows tilt-and-turn type, matched to existing façade windows, dimensions 200 x 126 cm replacing old windows and 60 x 80 cm toilet windows.

Office doors include wooden office doors (90 x 205 cm). Hardware includes stainless steel hinges, locks, and handles, with frames to accommodate partition wall type W112.

As per  EN 14351-2 – Internal Doors Standard

Sanitary fixtures include washbasins with taps, toilet seats with flush cisterns and built-in bidet, a low-mounted 10-liter boiler, and wall-hung mirrors sized 600 x 400 mm.

Existing condition - interior of the building

Existing condition – exterior view

#### Vehicle Inspection Pit

The inspection pit shall be constructed within the existing asphalted area as indicated in the dwg.

Pit dimension:

- clear depth min 1.7m

- clear width min 1.1m

- Length: 7m

- Metal ladder on the short side to access the pit.

- Covered with steel structure roof, similar to parking spots.

It will be used for inspection of armoured ambulance vehicles with dimensions:

Length: 665

Width: 265cm (wheels axle 207.5)

Height 305cm

Weight approx.: 12 T

Refer to site layout for position of the pit – conceptual design of the pit

The pit walls and floor shall be formed in reinforced concrete designed to withstand imposed vehicle loads and prevent structural failure. The pit dimensions shall allow safe access and ergonomic working conditions for personnel.

Concrete grade shall be suitable for heavy-duty applications with reinforcement designed in accordance with Eurocode standards. The pit floor shall be cast with a waterproof membrane and slope towards drainage channel to prevent water accumulation.

If the drainage system is higher than the pit floor level, the specification must include a dedicated pump.

The pit vehicle parking surface shall be reinforced slab with ramps on both sides.

Covered with steel structure and illuminated with LED lights ficed to the structure.

### Fuel Station

The fuel station point shall be organized and constructed at the top north corner of the compound, in accordance with the preliminary designs provided. The designated area is currently asphalted.

All power supply, IT, and water connections related to the fuel station shall be executed under their respective discipline sections within this document and the associated BOQs.

Fuel Tank and Slab Construction:

The fuel tank system shall comprise of a 30,000-liter fuel tank, including, Containment tank and cover, Fuel pump, RFID post and are to be provided and positioned on site by EULEX fuel contractor. These works are not to be included under the price.

The contractor shall be responsible for the following civil works:

- Supply of materials and construction of a reinforced concrete slab.

- Installation of precast concrete curb stones, size 24/18–12 cm, installed around the full perimeter of the slab

- The slab and curb stones shall be designed and executed to accommodate fuel station operational loads and equipment.

Ducting for Fuel and RFID Services:

The contractor shall supply and install the following ducting:

2 × Ø75 mm ducting pipes arranged as follows:

- from the fuel tank outlet to the fuel pump

- from the fuel pump to the RFID post

Ducts shall be continuous, properly sleeved, and positioned to allow installation of fuel pipes and RFID cabling without obstruction

Fuel Operator Office Container

A 10-foot office container/cabin (254 × 244 cm) shall be:

- Provided by EULEX

- Installed by the contractor over concrete blocks, positioned and levelled as per design requirements.

The contractor shall also provide:

- Steel access stairs, min 100 cm wide

- Estimated two risers, with a maximum riser height of 17 cm

- Complete fixing, anchoring, and safety compliance of the stairs.

Drainage and Environmental Protection

The contractor shall design, supply materials for, and construct a complete linear grilled drainage system for the fuel station area, in accordance with the preliminary designs, including:

- Linear trench drains with steel grating (heavy traffic loads)

- Proper slopes and connections

- Installation of an oil separator suitable for fuel station operations

- Connection to new drainage system for the Compound.

Oil separator capacity and final layout shall be presented for approval prior to commencement of any works on site.

Construction of Green Area Behind Fuel Tank:

The works shall include the cutting and removal of the existing asphalt surface, excavation to the required depth, and disposal of all debris off-site.

The contractor shall supply and place suitable soil and all necessary materials to construct a landscaped green area at the rear of the fuel tank, in accordance with the approved layout.

The total estimated area, based on the provisional layout, is approximately 57.5 m², with an associated perimeter length of 47.5 linear meters.

The scope of work shall comprise, but is not limited to:

- Saw-cutting and breaking of existing asphalt surface

- Excavation to formation level, including trimming and leveling

- Removal and legal disposal of asphalt, excavated material, and debris from site

- Supply, placing, spreading, and compaction of suitable soil for green area formation

- Supply and installation of precast concrete curb stones, size 24/18–12 cm, along the full perimeter.

- Final grading and preparation of the surface for landscaping works.

### Other

Covered parking spots:

There shall be four parking positions that needs covering, marked in overall layout as “A”, “B”, “C”  (C is repeated 2x)

Cover “A” for large vehicles – 27.5mx7m:

Prior to commencing any manufacturing contractor is to prepare and present designs including static calculations according to which the steel elements are to be dimensioned.

Quality of the steel used for the steel structure is to meet the requirements of the following standards EN 10 025/S235JR.

A form steel trusses leaning on square steel columns.

All the steel elements are to be cleaned first and painted with anti-rust/base coats of paint in two layers; painting of any welding spots is to be carried out after assembling/welding on site also in two layers.

Final painting to be done with oil paint, blue, in two layers, reaching a uniform color throughout the entire structure.

Reinforced foundation of the main columns.

10 cm sand bed is to be provided/placed and foundations are to be filled using concrete C 30.

Roof covering is to be done using trapezoid pre painted corrugated metal sheet, 0.55mm thick, color RAL 9002, including roofing ridge cap and snow guards, installed over metal purlins.

Roof is to be completed with horizontal and vertical gutters installed, including flashings.

All parts (union brackets, running outlets, stopend internal, pipe clips, offset bend, etc) are to be of the same material as the gutters and downpipes.

There shall be LED lights installed for illumination on the roof structure and also simple charging sockets for vehicle batteries, refer to electrical specifications.

Cover “B” – 31.5x6m:

For this cover EULEX will provide roof trusses and columns. Contractor is to carry installation of the same, foundation, paint the steel structure, provide and install prepainted sheets with gutters.  Refer to type “A” foundation and roofing materials for specifications.

Cover “C” – 6mx6m:

Same as cover B, EULEX is to provide roof trusses and columns, contractor is to carry the installation of the same, paint the steel structure provide and install prepainted sheets with gutters. Refer to type “A” foundation and roofing materials for specifications.

Flag poles:

Provide and install steel flag poles of 7.0 meters height above finished ground level complete with  raising and lowering mechanism. The poles shall be manufactured from hot‑dip galvanized steel suitable for outdoor use and long‑term corrosion resistance. The flag poles shall be installed on properly designed concrete foundations sized to withstand prevailing wind. One is to be positioned beside Commander Block while the other two as indicated in the site layout in the Grand Parade area.

### Dismantling of office blocks in old ECM Compound

Once RFPU is relocated from the existing Compound the following two blocks will be dismantled and structures of the same will be used for remaining blocks to be build, refer to Gant chart provided with tentative scheduling of works.

#### Dismantling of Block RN

Block RN consists of 19 office containers (605x244cm) and 3  of 20’ ablution containers  (605X244cm). Organised in two floors with steel structure corridors on both levels, internal and external steel staircases.

Facade/insulation is to be cut at the connection point of containers and removed from the facade panels/structure releasing the containers for dismantling.

Containers are welded among them on the lower and upper beam.

Any Barcoded item/asset such as containers itself, rack cabinets, AC Units, boilers are to be handed over to EULEX Representatives while all the debris to be removed from site to a designated dump site.

Containers once dismantled, are to be made free of all the wall panels leaving only the roof structure installed, floor layers are to be dismantled as well (PVC layer, plywood, insulation, plastic sheet, metal sheet).

Structure is to be preserved for reuse. Dismantling is to be done with due care, so the steel structure of containers is preserved.

Power supply: All electrical installations in the building are to be dismantled and disposed. EULEX Electrician will assist to disconnect the building from the main power line.

Fire Alarm: EULEX will disconnect the fire alarm from the main system. Installation/wiring is to be dismantled and disposed by contractor.

CIS: Rack cabinets complete will be withdrawn by EULEX, all other connections/cabling to be dismantled and debris removed from site.

Proper equipment, tools, scaffolding are to be used for dismantling works with specific attention to Health and Safety for the working team and users of the Compound.

See provided dwg showing the floor plans of the building.

This block is equipped with central heating system with radiators, EULEX technician will disconnect the premises from the main connection, Contractor is to dismantle all the radiators and piping running in the premises and remove debris from site.

Block has 2 ablution units of 20’.

Plumbing: EULEX Plumber will disconnect the building from the main networks (water and sewerage). Contractor is to carry any interior dismantling works related to sewerage and water from all ablution units including partitions, sanitary, etc.

View of RN Block

#### Dismantling of Block O1

Block O1 consists of 26 office containers (605x244cm) and 8 of  10’ ablution unit (244X255cm). Organised in two floors with steel structure corridors on both levels, internal and external steel staircases.

Refer to point 4.2.10.1  for details due to general similarities.

See dwg and picture below.

This block is equipped with central heating system with radiators, EULEX technician will disconnect the premises from the main connection, Contractor is to dismantle all the radiators and piping running in the premises and remove debris from site.

Block has 2 ablution units of 20’.

Plumbing: EULEX Plumber will disconnect the building from the main networks (water and sewerage). Contractor is to carry any interior dismantling works related to sewerage and water from all ablution units including partitions, sanitary, etc.

View of O1 Block

#### Refurbishment of steel structure for all office and ablution containers

For all the containers after dismantling the following works are to be carried to prepare the steel structure for further use.

The steel structure is to be thoroughly cleaned by removing any rust or loose materials.

Use wire brushes, sanding or grinders to clean off loose rust.

Make sure all weak, flaky, or loose steel is removed.

Apply Anti-Corrosion Primer through the whole structure.

Make sure all the connection points of container structure elements are tight (bolts/washers).

Notify representative of Contracting Authority if any major damage to the structure is noticed.

Note: the roof panels are to remain in place to keep the structure more firm due to transportation.

Floor: Clean and treat the floor steel structure the same way as the exterior main steel structure.

Apart from the main structure beams of the container the flooring of the containers is divided in 60cm segments with steel profiles running on the short side.

Provide and install galvanized metal sheet on the lowest level of the container as support for new layers to be installed at a later stage.

Galvanized metal sheet th= 0.8 mm bended in corners or supported by L flushing and fixed to the floor profiles.

#### Transportation of containers.

Once containers structures as described above are ready, the same are to be transported from Mitrovica Old Compound to the new location in Mitrovica, estimated distance 4 KM.

Due care is to be taken during transportation for safe loading, unloading and transportation of the same with use of proper equipments and machinery.

When loading and unloading attention is to be paid to the point of lifting whether through forklift pockets or corner castings dedicated for lifting to not damage the structure.

The container is to be secured in the truck with heavy-duty ratchet straps, chains or by blocking and bracing.

Ensure the container cannot slide or shift during transport.

All containers are to be safely stored on site in Mitrovica as per Instructions of Representative of Contracting Authority.

## Infrastructure/Horizontal Services

Preparation of ground has been implemented by EULEX as phase one of the project. (1st phase ground preparation has included excavation, geotextile, 0-150mm, 0-63mm and 0-31.mm gravel)

The site will be cleared, compacted with sublayers with around 80MN/m2 at the time of handover to contractor.

Contractor will be provided with the preliminary site layout and levels intended to be achieved, slope.

However it remain for the contractor to review and revise the preliminary site layout as per condition on site and in coordination with final designs of the whole infrastructure of the Compound.

The contractor shall carry out all work with due care, ensuring that any impact on the overall site preparation is minimized.

All activities shall be executed in a manner that avoids unnecessary alterations to completed work.

Prior to commencement of any activities contractor is to carry its own site survey, verification of levels, slopes, etc.

After approval of designs contractor is to establish reference point for the project, mark foundations, utilities, and structural elements according to the approved designs.

Excavation of utility trenches:

Trenches shall be excavated to the required depth and width, as per approved designs of each discipline, side slopes or shoring shall be provided to prevent collapse.

All excavated materials shall be stockpiled for reuse or disposal.

A minimum bedding layer of 10cm sand shall be placed at the trench base levelled and compacted before any utility installation.

Pipes, ducks or conduits shall be laid. Before backfilling all utilities shall be tested

(pressure, leakage, continuity).

Backfilling shall commence with covering of pipes with sand, excavated material, and gravel to be provided by contractor to reach again the required compaction.

30cm below the finished surface color coded warning tapes are to be provided and installed all over the trench length.

Precast reinforced concrete manholes are to be provided and installed at designated intervals not exceeding 50m, at junctions and changes in direction, depending on the type of utility, heavy duty manhole metal cover included (standard heavy transport 25t).

For electrical, IT/Comms, cameras, Fire alarms, solar panels installations the same routing will be used from the Data Center/Transformer to each building, premises, equipment as per preliminary design for trenches/manholes. The inner trenches to be established shall be connected with already outer perimeter ring of installations in specific manholes as per preliminary designs.

All these services shall follow the same trench routing as per preliminary design. New trenches may be established during final design where required to ensure full functionality of all systems.

Ducts shall be laid in straight runs with gentle bends, minimum radius of curvature as per manufacturer’s recommendations.

Provide sufficient number of ducts to accommodate all required systems.

Ducts shall be laid with proper spacing to avoid interference and allow future access.

Spare ducts shall be installed for any possible future use.

Maintain required clearances between electrical, communications, and other utilities as per standards.

Crossings shall be arranged to minimize electromagnetic interference and allow safe maintenance.

Where ducts run parallel, separation shall be maintained.

The respective engineers shall determine the final trench alignment.

Adjustments shall be made to ensure compliance with standards and site conditions. Sewerage and drainage trenches shall be excavated with correct slopes to ensure gravity flow.

Engineers shall coordinate trench routes to avoid clashes with other utilities (electrical, IT/Comms, fire alarms, solar).

If and where the geotextile is damaged (which is already installed by EULEX as part of phase one) while opening the trenches the same is to be replaced and corrected.

In areas of heavy traffic such as roads and other were assessed that damage can be cause to underground pipes the same is to be foreseen to be covered with concrete layers and protected.

Considering the work to be carried out and changes that the site might endure during design and construction the contractor shall carry out final preparation works prior to paving and asphalting, including but not limited to provision/laying of approximately 20cm of gravel 0-31.5mm and additionally approximately 5 cm of sand both for roads and paved surfaces.

Final leveling and compaction of the prepared layers is required to ensure proper surface quality for subsequent works.

The contractor shall provide all required materials and execute the installation of curbstones in various sections, 20/8 cm and 25/8 cm dimensions, 24/18-12cm or 24/18-15cm., in full compliance with applicable standards and regulations.

Curbstones shall be of durable concrete, properly aligned, leveled, and securely fixed to ensure stability and long-term performance. Joints shall be uniform, and bedding shall be prepared to prevent settlement or displacement.

Pavements shall be constructed in accordance with applicable standards, using durable materials suitable for pedestrian and light vehicle traffic. Finishes shall be even, slip-resistant, and aligned with the overall site design.

Concrete slabs for data centers, generators and others, shall be cast with proper reinforcement, thickness, and curing practices to ensure structural integrity and long-term durability.

Asphalt works shall be executed with appropriate base preparation, compaction, and thickness to accommodate intended traffic loads.

Asphalting with mixture AB 16 in thickness of 8cm.

All sides of the damaged areas shall be cut in straight lines, existing asphalted area, using mechanical asphalt disc cutters: the contractor is to make a vertical cut to the existing asphalt in order to reinforce the joint and to prevent the easy breaking of the new asphalt. This operation shall be executed using mechanical self-water-cooled cutting machine. No hand cuttings shall be allowed.

Applicable Standards for Asphalt Materials and Testing:

Bitumen

EN 12591, EN 1426, EN 1427, EN 1425

Asphalt Mix

EN 12697-1, 2, 5, 8, 12, 30, 34, 35

Aggregates

EN 933-1, 933-5, EN 1097-2, 1097-5

Surface shall be smooth, free of defects, and compliant with roadwork standards.

Green Areas shall include excavation, removal of surplus, provision and placement of soil including planting of grass, plants.

Ground markings are to be carried with traffic zone marking paint, two components, chlorinated solvent base type.

Minimum requirements as indicated in preliminary designs.

Indicated in dwg are the final layers/pavements of the Compound as per preliminary designs

## Electrical Specifications

### General Electrical requirements

At the time of commencement of works on site there shall be a 630KVA Transformer with electrical meter installed for the Compound.

Two Backup Generators of 800KVA with ATS and fuel tank will be provided by EULEX and have to be integrated as backup within the electrical solution by Contractor.

The electrical installation shall be designed and installed in accordance with the applicable international and local standards, regulations, and codes of practice.

The Contractor shall be fully responsible for the design, supply, installation, testing, and commissioning of the complete electrical system required for the proper and safe operation of the Compound.

The Contractor shall prepare and submit all electrical designs, calculations, layouts, and technical specifications for review and approval prior to implementation.

All equipment and/or accessories not specifically mentioned in the specifications or not shown on the drawings, but which are obviously necessary for the proper and normal operation of the various systems, shall be included.

The Contractor shall provide and execute such works as part of the contract and shall not be entitled to any extra payment on this account.

Electrical materials and equipment shall be new, of high quality, and suitable for the intended purpose and environmental conditions.

All installations shall be executed by qualified personnel in a safe and workmanlike manner, ensuring reliability, efficiency, and ease of maintenance.

The electrical installation shall include, but shall not be limited to, power supply and distribution, lighting systems, grounding/earthing, protection systems, and any equipment required to support mechanical and operational systems.

Adequate protection shall be provided against overload, short circuit, voltage fluctuation, and environmental factors such as moisture, dust, and temperature variations.

All exposed electrical components shall be properly enclosed and protected.

The Contractor shall ensure proper coordination with other disciplines to achieve full integration of electrical systems within the facility.

All works shall be tested and commissioned to verify compliance with the design and performance requirements.

Upon completion, the Contractor shall provide all necessary documentation, including as-built drawings, test reports, and operation and maintenance manuals.

Preliminary route from Transformer to each building/equipment/item has been provided with the drawings sets.

Refer to ground works for trenches/ducting pipes.

All underground cables shall run through these trenches in adequate conduits pipes from transformer/main panels to building or other panels.

Underground cables shall be of aluminum conductor insulated as required (Al).

Sizing shall be determined by contractor based on engineering calculations.

All panels shall be as weatherproof enclosures, corrosion resistant, installed in safe and accessible areas. Labeled and secure. Suitable for exterior use.

Main electrical panels position as indicated in site layout. Grounding shall be achieved with copper rods or equivalent systems.

Building panels are to be installed on the exterior, fixed to their respective facades reachable for technicians at all times even when buildings are locked by building users for maintenance and intervention purposes.

There should be an internal electrical meter only for Cafeteria Building, to be able to control the consumption of the building.

This meter is for internal reading purposes for this building; however total consumption of the Compound is still to be with one electrical meter for all.

External Lighting:

Apart from perimeter lights already in place at the commencement of works, the contractor shall design, provide, install, and test the following:

- LED Floodlights: Approx. 50 W units mounted on galvanized poles fixed to building structures.

- Decorative LED Lighting: To illuminate the central parking and central landscaped green area (3-3.2m and 08-1m preferable).

- Helipad Lighting: LED spotlights installed over the T-walls on both sides to ensure visibility and safety.

- Sports & Recreational Areas: LED lighting provided for the Grand Parade, gym outdoor area, and basketball half court.

- Fuel Station.

- Covered areas (entry, vehicle parking, vehicle inspection pit).

All installations shall comply with applicable EU regulations, IEC/NEC standards, and best engineering practices. Fixtures must be weatherproof, energy-efficient, and positioned to ensure uniform illumination without glare.

Charging electrical sockets 220V:

Charging sockets for parked vehicles are to be provided for parking spots under shed “A” and “C” as indicated in site layout.

Weatherproof sockets suitable for exterior installations. Equipped with protective cover.

Sockets shall be mounted on posts or walls. Cabling is to be routed underground in conduits and trunking when coming overground to protect against mechanical damage.

Internal Electrical Installations:

For Container Blocks:

Cabling and Routing:  All external cabling supplying container units shall be concealed within facade works to maintain aesthetics.

Connections of containers shall be made with flexible cables sized according to the load (e.g., 5x6 mm² /5x2.5 mm²), routed from exterior internally into PVC distribution boxes.

Cabling inside containers shall continue covered with PVC conduit/trunking or concealed within suspended ceiling structures where applicable (corridor).

Container PVC Distribution Boxes- for each container:

Indoor PVC distribution boxes shall be mounted in accessible positions (ceiling near windows) and sized to accommodate required devices with at least 1x spare.

Typical minimum configurations include:

- 5 EA -16A fuses,

- 1EA - 20A fuse,

- Protection fid 3P/25A 300mA.

- 1xspare

Lights Installations:

Internal lighting installations shall be designed to provide adequate illuminance levels for safe and efficient use of office spaces, in compliance with EN 12464-1 and applicable EU regulations.

- Offices: LED surface-mounted fittings, natural white light, with cabling in PVC trunking, color temperature min. 4000K, luminous flux: min 3200lm, type of protection IP 20, min 40w, desirable dimensions 120x30cm suitable for container setup.

- Corridors: LED recessed fittings (approx. 60x60 cm) for suspended ceilings, cabling routed above ceiling same characteristics as office lights.

- Toilets: Slim LED surface-mounted fittings.

- Emergency Lighting: Exit signs and emergency luminaires.

- Main entries and exit covers: LED surface mounted lights outdoor.

Sockets:

Minimum 3 double sockets for single container

Minimum 5 double sockets for double container

Minimum 4 double sockets for ground floor corridor

Minimum 4 double sockets for 1st floor corridor

Minimum one single sockets for AC Unit / per container

Switches: single/double/alternative switches shall be installed in containers depending on the size and configuration.

Corridors and toilets shall be controlled with ceiling mounted sensors (360°)

Rack cabinet: Direct line from building electrical panel is to be provided for rack cabinets installed on each building.

Infirmary – Electrical Installations

Containers designated for the infirmary shall be new units, already equipped with electrical installations in accordance with their specifications.

Modifications shall be foreseen for containers used as emergency rooms, as these require additional sockets to support medical equipment.

Electrical installations in the emergency room shall be organized as separate circuits, enabling connection to an inverter for backup supply in the event of a power outage, thereby ensuring continuity of service during emergencies.

Other buildings:

All installations shall be executed in full compliance with applicable standards and regulations.

The type of sockets, light fixtures, switches, emergency lights, exit lights, outdoor lights and other related accessories shall be adapted to suit the occupancy and functional use of each building (whether GYM, workshop or other) Ex: usage of industrial high bay lights in transport or other depending on activity or application.

Some specifics apart from general requirements:

Cafeteria:

For the kitchen area, electrical connections should be designed and installed in accordance with the specific requirements of the kitchen equipment and appliances to be provided. Refer to list of all appliances with specifications and requirements and preliminary design.

Gym: Treadmills and other training equipments require power supply as well apart from other required electrical installations standard for the GYM Building.

MSD Building:

Attention should be given to the workshop area, where equipment is positioned, to ensure proper electrical connections are provided in accordance with each machine’s requirements.

The compressor shall be installed on the exterior of the building, as indicated in the preliminary design, and requires a three-phase electrical supply.

Sockets shall be aligned on the same level all around the machinery covered with PVC trunking.

There shall be light over each working bench fixed on the wall apart from overall ceiling hung lights suitable for transport workshop industrial high bay lights.

Refer to MSD Building – list of equipment that EULEX will position inside the workshop and the needs for connections.

Office sections within the MSD Building shall be equipped with sufficient number of sockets for AC Untis, office equipments and other depending on the purpose of use.

Data Center: Datacenter to be provided by EULEX also required electrical connection – 3 phase which is to be executed by contractor.

All electrical installations within the compound, whether specifically mentioned in the documentation or not, shall be designed, provided, installed, and tested by the contractor in full compliance with applicable EU regulations, IEC/NEC standards, and best engineering practices.

The contractor shall ensure that all necessary sockets, switches, lighting fixtures, distribution boards, cabling, protective devices, and related accessories are supplied and installed to meet the functional requirements of each building and area of use.

Any omissions or items not explicitly listed in the specifications but required for the safe, complete, and operational delivery of the electrical system shall be deemed included in the contractor’s scope of work.

## Mechanical Specifications

Design and Build of HVAC systems for the whole Compound is required.

The designs must be prepared referring to the data from the main architectural project, based also on climatic conditions of Mitrovica, and on technical standards for designing installations for similar buildings.

Contractor is to carry calculations, sizing of whole systems requirements and presenting specific designs and manufacturers specifications for approval prior to commencement of any works on site.

Internal Temperature: the internal temperature in all office and residential areas should be kept at an average of 22 º C, (+-2 degrees) at all times. This should exclude workshops (16 ºC (+-1 degree) and the Gym where the temperature should be kept at around 18 ºC (+-1 degree). Temperature regulation in individual blocks and rooms: Required

### Heating

The whole Compound has been thought to be divided into two Heating Stations, considering also the large spatial extent of the Compound, distance between buildings, different patterns of use of occupancy. For a large compound, multiple heating stations were considered more appropriate to improve efficiency, reliability, and adaptability. By reducing distances also, the heat loss is reduced, and efficiency is improved by lowering energy waste.

Station 01 is to cover:

- Block 1 / Platoon Accommodation Block

- Block 2 / Platoon Accommodation Block

- Block3 / Platoon Accommodation Block

- Block 4 / Female Accommodation Block

- Block 5 / Commander Block

- Block 6 / Office Block

- Building 8 / Recreation Building

- Building 16/MSD Building

Conceptual design of exterior pipeline route – Station 01

Station 02 is to cover:

- Building 9 / Training House

- Building 10 / Gym

- Building 11 / Cafeteria

- Building 12 / MSO Block

- Building 13 / Reception Block

- Building 14 / Infirmary Block

- Building 15 / Reserve Block

Conceptual design of exterior pipeline route – Station 02

Requirements for Heating System:

Heating Plant: Heat pump.

Source: Electricity

Heating process through: water circulating system

External: from the Station to Buildings to run underground with pre insulated heating pipes.

Internal: Copper pipes. Horizontal and vertical Copper tubes Cu inside the facility and the links to radiators shall be painted the same color as the radiators.

Heating bodies:   Radiators (with thermostatic valves) in bedrooms/offices/corridors/etc

As containers don’t easily accommodate complex ductwork, or four pipe systems and condensation drain due to structural constrains, radiators have been chosen as heating bodies with two pipes (supply/return). As radiators provide controlled room comfort during wintertime with no noise issues in small container offices.

Radiators will be fixed on appropriate holders depending on the type of units, positioned below windows. The number of holders is determined by the length of the unit. Holders with console should be placed on the walls.

- Calorifiers in storage/training/workshops/etc.

- Pipes: Steel pipes for these areas painted in gray.

Calorifiers will be fixed in trusses/roof structures or ceiling.

Maintenance requirements: as low as possible

Spare Parts & Technology: Should be possible to outsource locally.

At the entry point of each building there shall be control valves to switch off the heating system in case of potential leakages, interventions or other.

Buildings will be equipped with AC Units for individual cooling control of each room, as occupancy and usage vary.

AC Units are listed under buildings BOQs and specifications.

### Ventilation System – dining room in Cafeteria

Ventilation for Dining Room in Cafeteria: The contractor is to identify, carry out detailed project documentation and install/ implement a suitable technical solution that ensures the provision of adequate ventilation for the dining room and appropriate conditions for the users.

System is to have switches with regulator.

All the required materials, equipment and manpower are to be provided by contractor.

### Exhaust hood /ventilation for kitchen in Cafeteria

A proper ventilation hood is to be manufactured, provided and installed for the kitchen island cooking area in order to maintain comfortable working conditions.

Ceiling mounted/hung cubic hood is to be  stainless steel equipped with labyrinth filters and motor. Designed as per kitchen layout and equipments.

### Fans /Ventilators for MSD Building / stores&workshops

Installed on the facade wall, balanced and low-noise operation, corrosion-resistant construction, adjustable frequency, suitable for use in stores/workshops, equipped with all the required accessories (mesh, wall mounting frame, louver shutter).

### Bathrooms extract fans other areas

Units to be provided and installed where and as required.

The unit shall be with ultra-low noise performance, silent. Wall mounted, suitable for continuous or intermittent operation , models suitable for connection to 100 mm / 120 mm / 150 mm duct, with external grid or louver.

## General Plumbing/Hydraulic Specifications

The Contractor shall design, supply, install, test, and commission all plumbing and hydraulic systems required for the complete operation of the Compound, including all pipework, fittings, valves, equipment, and accessories.

The systems shall be designed as fully integrated installations ensuring safe, efficient, and reliable distribution of potable water and discharge of wastewater, drainage.

The Contractor shall be fully responsible for:

- Hydraulic design calculations (flow rates, pressures, pipe sizing)

- Preparation of: Layout drawings, Isometric drawings, Installation details

- Coordination with architectural, structural, and other systems

Ensuring adequate access, clearance, and maintainability.

All systems shall comply with:

Relevant European Standards (EN) and/or DIN standards

WHO guidelines for potable water

Applicable Kosovo Law and Regulations and Administrative Instructions

### Water Supply

Water Meter: The main supply water meter will be in place, to which the network to be designed is to be connected.

EULEX is to provide 6x5000ltr second hand water tanks which are to be integrated before the filtering system as backup in case of water cuts.

Filtering System:

The contractor is to design, supply, and install a filtering system at the entry point of the Compound. This system will treat incoming water from the city network (Mitrovica Municipality) and produce water suitable for human consumption.

Capacity of usage for maximum 200 people, accommodated 24x7 withing the compound.

The filtration system must be fully integrated, automated, and operational. It shall include all components necessary for proper operation, even if not explicitly listed.

System sizing is to be based on the required daily consumption, considering the maximum occupancy of the Compound — 200 people for 24 hours of accommodation needs.

Water supply → Storage tank → Filtration system → Users (potable water)

Upon installation of the filtration system, the water shall be tested. Water quality testing is to be carried by an accredited laboratory after installation, with certification that it meets potable standards.

Exterior Network:

Materials and Installation:

The contractor shall select appropriate materials for all external system installations. Polyethylene (PE) pipes shall be used for underground water distribution. Pipe sizing shall be determined based on hydraulic calculations.

All materials and accessories shall be durable, corrosion-resistant, and approved for potable water use.

Hot Water Supply:

Hot water shall be available at each basin, shower, sink, and other required fixtures. Hot water shall be provided through appropriately designed electrical heating units.

Heating units should be arranged at the most economical advantage to ensure immediate hot water availability.

Cold Water Supply:

Cold water shall be available at each basin, shower, sink, equipment, and other required points as defined in the final design.

Additional Water Supply Requirements:

In addition to Building Sanitary Units (toilets, showers, kitchens, kitchenettes, laundries, and other system equipment), water supply shall also be provided for:

- The Datacenter Container cooling system.

- Exterior connections for water hoses, including at the Fuel Station. A minimum of two additional exterior connection points located at different angles of the Compound.

- Heating Plant Units and other equipments

General Requirements: All installations shall comply with applicable standards and regulations for potable water systems.

The contractor shall ensure that all systems are fully operational upon completion and testing.

Internal Network:

The internal water network shall include the connection of all sanitary fixtures within ablution units, kitchens, laundry rooms, and other facilities requiring water supply.

Reference shall be made to the building conceptual and preliminary designs for the indicated locations and quantities.

Each Building shall be equipped control valves at the entry point for possible disconnection of the water supply for that building only in case of breakdown or intervention.

### Sewer System and Wastewater Treatment Plant

The Contractor shall be responsible for the design, provision, installation, testing, and commissioning of a complete sewerage system for the compound, including internal and external networks, a biological treatment plant, and final discharge.

The system shall ensure the safe and hygienic collection, conveyance, treatment, and disposal of all wastewater generated within the compound, in compliance with applicable environmental, health, and regulatory requirements.

Internal Sewerage Network:

The internal sewerage network shall include the connection of all sanitary fixtures within ablution units, kitchens, laundry rooms, and other facilities requiring sewerage discharge.

Reference shall be made to the building conceptual and preliminary designs for the indicated locations and quantities.

All wastewater generated within the buildings shall be conveyed by gravity to the external sewerage network.

Pipes shall be of PVC material and shall be properly sized in accordance with hydraulic design calculations.

All pipes shall be watertight, durable, and resistant to corrosion.

External Sewerage Network:

The external sewerage network shall collect wastewater from all buildings and premises within the Compound and convey it to the septic / collection tank and subsequently to the Wastewater Treatment Plant.

The system shall consist of underground  PVC pipes or equivalent approved materials, sized based on hydraulic calculations to ensure adequate capacity and self-cleansing velocities.

Manholes shall be installed at appropriate locations, including changes in direction, changes in pipe diameter, junctions, regular intervals along straight runs.

Manholes shall be constructed of prefabricated concrete elements and shall be fitted with heavy-duty covers suitable for traffic loads (40t)

A septic/collection tank shall be constructed as a primary treatment unit upstream of the biological treatment plant.

The septic tank shall receive all wastewater from the external sewerage network it shall be watertight and adequately sized based on the design population and wastewater flow.

Effluent from the septic tank shall be pumped to the biological treatment plant. Sludge accumulated in the septic tank shall be periodically removed and disposed of in accordance with regulations.

Wastewater from kitchens should be channelled through a grease interceptor to prevent fats, grease and other frying oil residues from entering the sanitary sewer.

Prefabricated Overground Biological Treatment Plant:

An overground prefabricated biological wastewater treatment plant shall be supplied and installed for the treatment of all wastewater generated within the compound.

The treatment plant shall be designed for a maximum capacity corresponding to 200 personnel accommodated in the compound on a 24/7 basis.

The treatment process shall include appropriate biological treatment technology to achieve the required effluent quality standards.

The plant shall operate reliably under variable load conditions

Be accessible for operation and maintenance

Include all necessary mechanical, electrical, and control components

Discharge:

Following final treatment, the treated effluent shall be conveyed to the designated discharge manhole and discharged into the river.

The discharge system shall:

Ensure compliance with applicable environmental standards

Prevent erosion and environmental damage at the discharge point

Provide controlled and safe release of treated effluent

No untreated or partially treated wastewater shall be discharged into the river.

### Drainage System

The Contractor shall be responsible for the design, supply, installation, testing, and commissioning of stormwater drainage system for the Compound.

The system shall ensure the effective collection, conveyance, and discharge of stormwater from buildings, roads, and paved areas without causing flooding, ponding, or structural damage.

The stormwater drainage system shall include all necessary components for surface and subsurface water collection, including, but not limited to, perforated drainage pipes around buildings, solid conveyance pipes, manholes, catch basins (gullies), and associated fittings.

Perforated drainage pipes shall be installed around building perimeters to collect groundwater and infiltrated surface water.

These pipes shall be properly bedded, surrounded with suitable filter material, and wrapped in geotextile to prevent clogging. They shall be connected to the main stormwater drainage network through appropriate collector pipes.

Adequate drainage shall be provided along the main roads within the Compound.

The system shall include also side channels or kerbs, and road gullies (catch basins) installed at appropriate intervals, all connected to the main drainage network.

Given that the Compound is located at a lower elevation than the main road, particular attention shall be paid to the design to prevent inflow of external surface water into the Compound.

More critical areas are east and south side of the Compound which are to be taken into consideration. Appropriate drainage measures shall be implemented to intercept and divert incoming runoff.

Reference shall be made to the site layouts and existing site conditions during the design and execution of the works.

Pipe diameters shall be determined based on hydraulic calculations. Pipes shall be constructed of high-density polyethylene (HDPE/PE) or equivalent material, with adequate stiffness class suitable for the intended installation conditions.

Manholes shall be provided throughout the network for inspection and maintenance purposes. They should be constructed using prefabricated concrete elements and fitted with heavy-duty covers designed for a minimum load capacity of 40 tons.

Gullies shall be fitted with ductile cast iron or composite gratings complying with EN 124, with a minimum load class of D400 (40 tons) for areas subject to vehicular traffic.

Oil separator is to be included for the area covering Transport workshop and Vehicle Inspection pit.  Also, the fuel station drainage area is to be connected to this system after the oil separator outlet as described herein this document.

All collected stormwaters shall be conveyed through the system and discharged via existing drainage manholes located in the Compound.

### Rainwater collection and reuse system Specifications

The Contractor shall design, provide and install a complete rainwater collection and reuse system.

The system shall consist of buried polyethylene storage tank and include all necessary components to ensure full functionality, durability, and compliance with applicable standards and regulations.

The system shall be designed to collect rainwater from a catchment area of approximately 1500–1700 m².  Tank sizing shall be based on local rainfall data / surface area to cover.

Upon reaching maximum storage capacity, excess rainwater shall be discharged through a controlled overflow system into the nearest manhole.

The rainwater reuse system shall include all necessary pumping, control, and distribution components to enable its intended use (irrigation mainly or other non-potable applications).

All relevant environmental, health, and sustainability requirements shall be complied with.

The Contractor shall provide all accessories, valves, connections, and maintenance provisions necessary to ensure safe operation, accessibility, and long-term performance of the installation.

The system shall include controlled outlets to the nearby green area, which will be used for irrigation.

## IT and Communication Specifications

### Network Infrastructure – Mitrovica Camp

#### Outdoor Fiber Optic Backbone Cabling:

Scope: Outdoor fiber optic backbone cabling between Data Center and buildings

Topology: Redundant ring topology 
Fiber Type: OM4 multimode (12-core)
Application: Inter-building backbone connectivity (10Gb capable)

The Contractor shall deliver a complete and fully operational outdoor fiber backbone system, including:

- Route verification and coordination

- Supply of all fiber-optic materials

- Outdoor installation in trenches

- All fiber cables need to be installed in dedicated protective pipes. Protective pipes to be included in the pricing.

- Fusion splicing and jointing

- Fiber termination at Data Center and buildings

- Installation of fiber patch panels and splice closures

- Labeling, testing, certification, documentation, and commissioning

The Lump-Sum Price shall be fully inclusive. No additional costs or claims shall be accepted.

- Network Architecture

- Three (3) redundant OM4 fiber rings interconnecting buildings and the Data Center.

Exact paths outlined in the Preliminary Compound layout and rings path.

- One (1) direct fiber link from the Data Center to the Space for the Grand Parades

- Self-healing ring topology providing path redundancy and fault tolerance

- Fiber Cable Specifications

- Type: OM4 Multimode Fiber

- Core Count: 12 cores

- Standards: ISO/IEC 11801, ANSI/TIA-568

- Construction: Outdoor-rated, armored, moisture- and rodent-resistant

- Installation Requirements

- Installation in underground trenches

- Excavation and trenching are included under the Ground works for the Compound.

- Manufacturer limits for bend radius and pulling tension shall be respected

- Minimum separation from power cabling shall be maintained

- Splicing and Termination

- Fusion splicing only

- Outdoor-rated splice closures

- Rack-mounted fiber patch panels with LC duplex adapters

- Proper strain relief and cable management

- Labeling

All fibers shall be labeled at both ends, patch panels, and splice closures.

Label example:

DC-R1-B05-F07

(Data Center – Ring 1 – Building 05 – Fiber core 07)

- Testing and Certification

- OTDR testing (bi-directional)

- Power meter / light source testing

- Compliance with OM4 loss budgets

Failed links shall be corrected and retested at no additional cost.

- Documentation and Handover

The Contractor shall provide:

- OTDR traces (PDF and native format)

- Power loss test results

- Fiber core allocation table

- As-built diagrams

- Splice records and labeling schedules

Provisional / final acceptance is conditional upon full documentation delivery.

- Indicative Quantities (Guidance Only)

- Approximate total fiber length: 1,527 meters

- Fiber type: OM4 multimode, 12-core

- Quantities are indicative only and shall not affect the total lump-sum price

- Exclusions

- Trenches and Excavation – which are to be priced under ground works BOQ.

- Active network equipment

- Power and UPS systems

- Indoor CAT6 cabling

Qualifications

- Legal Status: Legally registered company authorized to perform fiber‑optic or telecommunications infrastructure works, with valid business registration and tax compliance.

- Relevant Experience: Minimum three (3) years experience in outdoor fiber‑optic installations and at least two (2) similar projects completed within the last five (5) years, including underground fiber installation, fusion splicing, and testing.

- Technical Capability: Availability of qualified personnel experienced in OM4 multimode fiber installation and fusion splicing, and access to appropriate equipment (fusion splicer, OTDR, power meter).

- Standards Compliance: Ability to perform works in accordance with applicable international standards (ISO/IEC 11801, ANSI/TIA‑568) and manufacturer recommendations.

Compound layout and rings path

Ring 1- marked in Light Blue: DC → B1 → B2 → B3 → B4 → B5 → B6 → B7 → B8 → DC
Ring 2- marked in Red: DC → B11 → B10 → B09 → B16 → B17 → B18 → DC
Ring 3- marked in Yellow: DC → B12 → B13 → B14 → B15 → B19 → DC

| Building # | Building Name | Cabinet | Fiber panel | Connections Fiber |
| --- | --- | --- | --- | --- |
| 1 | Platoon Acc Block 1 | 1 medium | 1 (4 port) | 2 |
| 2 | Platoon Acc Block 2 | 1 medium | 1 (4 port) | 2 |
| 3 | Platoon Acc Block 3 | 1 medium | 1 (4 port) | 2 |
| 4 | Female Acc Block | 1 small | 1 (4 port) | 2 |
| 5 | Commander Block | 1 small | 1 (4 port) | 2 |
| 6 | Office Block | 1 small | 1 (4 port) | 2 |
| 7 | FPU Storage | / | / |  |
| 8 | Recreation | / | / |  |
| 9 | Training | 1 small | 1 (4 port) | 2 |
| 10 | Gym | / | / |  |
| 11 | Cafeteria | / | / |  |
| 12 | MSO Block | 1 small | 1 (4 port) | 2 |
| 13 | Reception | 1 small | 1 (4 port) | 2 |
| 14 | Infirmary | 1 small | 1 (4 port) | 2 |
| 15 | Reserve Block | 1 medium | 1 (4 port) | 2 |
| 16 | MSD Building | 1 medium | 1 (4 port) | 2 |
| 17 | Cleaning Staff and others | 1 small | 1 (4 port) | 2 |
|  | Server Room (Containerized Datacenter) |  |  | 6 ( 2 connections for each ring) |
|  | Space for the Grand Parades |  |  | 1 Fiber connection from Server Room |
|  |  |  | Total connections | 33 |

#### Indoor Horizontal Structured Cabling (UTP)

Design, supply, installation, testing, certification, and commissioning of indoor horizontal UTP structured cabling for multiple buildings located within Camp Mitrovica.

Each building shall be wired internally from the Intermediate Distribution Frame (IDF) network cabinet to end‑user dual RJ45 outlets.

1. Scope of the work

- Supply and installation of Cat6 UTP cabling

- Horizontal cabling

- Supply & installation of:

  - Patch panels

  - Cable management

  - Dual port RJ45 outlets

  - Faceplates and back boxes

  - Cat6 UTP Cable

- Cable containment (PVC conduit / cable trays)

- Termination, labeling, testing, and documentation

- Network cabinets will be provided by EULEX. Therefore, the scope DOES NOT INCLUDE supply of:

  - Network cabinets

  - Cabinet power distribution units

  - Any networking equipment (switches, routers, etc.)

- A total of 13 inter-building short distance UTP connections to be installed. Price to include underground protection pipe and terminations. Price to be included in the per single connection (Price unit).

2.      Definition of “Single connection”

For the purpose of this tender, one (1) Single Connection is defined as a complete, tested, and certified horizontal structured cabling link between one patch panel port located in the IDF cabinet and one dual RJ45 information outlet at the work area.

The price per Single Connection shall be all‑inclusive and shall cover, at minimum:

- Category 6 UTP cable (up to 90 m horizontal length)

- Cable containment (PVC conduit, trunking, accessories)

- Dual RJ45 Cat6 outlet including keystones, faceplate, and back box

- Patch panel port and termination

- Cable management within cabinet

- Termination, labeling, and identification at both ends

- Testing and certification

- Documentation and as‑built records

- Labor, tools, consumables, and waste disposal

No additional charges shall apply beyond the quoted unit price.

4. Technical Specifications

- Cable Type: Category 6 UTP

- Standards: ANSI/TIA-568, ISO/IEC 11801

- Maximum horizontal cable length: 90 meters

- Topology: Star Topology

- Termination standard: T568B

- All installed components shall comply fully with the applicable standards and be compatible as a complete structured cabling system.

5. Installation Requirements

- Proper separation from power cables

- No splices allowed in horizontal cabling

- Cable bend radius to comply with manufacturer specs

- All terminations to be neatly dressed and labeled

- Any installation not complying with these requirements shall be rectified by the Contractor at no additional cost to EULEX.

6.Testing & Acceptance

- 100% of installed UTP links shall be tested and certified

- Testing shall be performed with a calibrated cable analyzer compliant with Cat6

- Test results shall show PASS status for each permanent link

- All test results shall be submitted electronically in PDF format

- Failed links shall be rectified and re-tested at no additional cost

- EULEX reserves the right to witness testing or request sample re-tests

| Building # | Building Name | Building Type | Story | Area (m2) per floor | Cabinet | RJ45 Patch panel | Connections UTP | Cable management |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Platoon Acc Block 1 | Containers | 2 | 305.47 | 1 medium | 3 (48 port) | 128 (64 dual outlets) | 4 |
| 2 | Platoon Acc Block 2 | Containers | 2 | 305.47 | 1 medium | 3 (48 port) | 128 | 4 |
| 3 | Platoon Acc Block 3 | Containers | 2 | 305.47 | 1 medium | 3 (48 port) | 128 | 4 |
| 4 | Female Acc Block | Containers | 2 | 123.06 | 1 small | 1 (48 port) | 44 | 2 |
| 5 | Commander Block | Containers | 2 | 169.58 | 1 small | 2 (48 port) | 62 | 3 |
| 6 | Office Block | Containers | 2 | 237.41 | 1 small | 3 (48 port) | 100 | 4 |
| 7 | FPU Storage | Containers | 1 | 100.00 | / | / | 2 UTP from Office Block | / |
| 8 | Recreation | Modular | 1 | 127.00 | / | / | 2 UTP from Office Block | / |
| 9 | Training | Modular | 1 | 200.11 | 1 small | 1 (48 port) | 16 | 2 |
| 10 | Gym | Modular | 1 | 503.75 | / | / | 2 UTP connection s from Training | / |
| 11 | Cafeteria | Modular | 1 | 250.64 | / | / | 2 UTP connections from MSO | / |
| 12 | MSO Block | Containers | 1 | 137.53 | 1 small | 1 (48 port) | 40 | 2 |
| 13 | Reception | Containers | 2 | 44.29 | 1 small | 1 (48 port) | 28 | 2 |
| 14 | Infirmary | Containers | 1 | 174.56 | 1 small | 1 (48 port) | 34 | 2 |
| 15 | Reserve Block | Containers | 2 | 407.29 | 1 medium | 4 (48 port) | 178 | 5 |
| 16 | MSD Building | Concrete | 2 | 833.96 | 1 medium | 3 (48 port) | 96 | 3 |
| 17 | Cleaning Staff and others | Container | 1 | 121.37 | 1 small | 1 (48 port) | 26 | 2 |
| 18 | Fuel Station | Container | 1 |  | / | / | 4 connections from cleaning container | / |
| 19 | Compressor container | Container |  |  | / | / | 2 connections from Reception | / |
|  | Heating Plant | Container |  |  | / | / | 1 connection to Heating Plant from Server Room | / |
|  | Fuel tank |  |  |  | / | / | 1 connection to Fuel Tank from Server Room | / |
|  | Generators | Containerized |  |  | / | / | 2 connections to Generator 1 and 2 from Server Room | / |
|  | Server Room | Containerized Datacenter |  |  |  |  | 4 ( to be excluded from calculations) |  |
|  | Space for the Grand Parades | Panel /open space |  |  |  |  | 1 UTP from Commander Block |  |
|  |  |  |  |  |  | Total connections | 1029 |  |

In the following floor plans single dot marking represents a double RJ45 outlet.

Block 1 - Platoon Accommodation Block

Block 2 - Platoon Accommodation Block

Block 3 - Platoon Accommodation Block

Block 4 - Female Accommodation Block

Block 5 - Commander Block

Block 6 – Office Block

Block 7– FPU Storage

2 UTP connections from the Office Block

Building 8 – Recreation

2 connections from the Office Block

Building 9 – Training

Building 10 - Gym

2 connections from the Training House

Building 11 – Cafeteria

2 connections from the closest cabinet

Block  12 - MSO Block

Building 13 – Reception

Building 14 – Infirmary

Building 15 - Reserve Block

Building 16 – MSD Building

Building 17 - Cleaning Staff and others

Building 18 – Fuel Station

2 connections from the cleaning cabinet

Building 19 – Compressor container

2 Connections from the Reception

Building – Heating Plant, Fuel tank, Generators, Server Room (Datacenter)

1 connection to Heating Plant, 1 connection to Fuel Tank, 2 connections to Generator 1 and 2

Building – Space for the Grand Parades

1 UTP connection from Commander Block to Space for the Grand Parades

### CCTV Network Infrastructure:

The CCTV Network Installations in the New Camp are mainly to be implemented by EULEX as marked in red in the Camp Layout below.

However, there are a number of Inner Cameras for which the Internal perimeter cabling and infrastructure is to be established, and EULEX will provide and install the Cameras once connections/positions are ready.

Infrastructure of Cameras marked in blue (PTZ) and Yellow (dome) marked in the below layout is to be considered part of this tender dossier.

It is to include provision, installation, testing, certification, and commissioning of horizontal UTP structured cabling for the CCTV inner perimeter located at Camp Mitrovica.

Locations and Technical Requirements

PTZ Cameras (Five Units - marked in blue):

Platoon Block #01

- Metal pipe is to be mounted at the highest point (approximately 3 meters)

- CAT6 UTP cable length: estimated 35 meters

- Cable containment: PVC conduit / cable trays

Reserve Block #15

- Metal pipe is to be mounted at the highest point (approximately 3 meters)

- CAT6 UTP cable length: estimated 30 meters

- Cable containment: PVC conduit / cable trays

Cafeteria #11

- Metal pipe mounted at the highest point (approximately 3 meters)

- CAT6 UTP cable length: estimated 35 meters

- Cable containment: PVC conduit / cable trays

Gym # 10

- Metal pipe mounted at the highest point (approximately 3 meters)

- CAT6 UTP cable length: estimated 35 meters

- Cable containment: PVC conduit / cable trays

MSD Building #16

- Metal pipe mounted at the highest point (approximately 3 meters)

- CAT6 UTP cable length: estimated 30 meters

- Cable containment: PVC conduit / cable trays

Dome Cameras (Eleven Units – marked in yellow)

Main Gate (Three Cameras – connected to the Reception Switch)

- Each camera mounted on the perimeter fence at a height of 3-4 meters

- CAT6 UTP cable length: estimated 35 meters per camera

- Cable containment: PVC conduit / cable trays

Pedestrian Entrance (Two Cameras – connected to the Reception Switch)

- Each camera mounted on the building facade

- CAT6 UTP cable length: estimated 10 meters per camera

- Cable containment: PVC conduit / cable trays

Ammunition Depot # 19 (Two Cameras – connected to the Infirmary Switch)

- Each camera mounted on a T-wall or metal pipe

- CAT6 UTP cable length: estimated 40 meters per camera

- Cable containment: PVC conduit / cable trays

Helipad Reload Area (Two Cameras – connected to the Infirmary Switch)

- Each camera mounted on a metal pipe/fixed on T walls in accordance with Security and Safety requirements

- CAT6 UTP cable length: estimated 40 meters per camera

- Cable containment: PVC conduit / cable trays

Fuel Station (Two Cameras – connected to the outer perimeter switch)

- Each camera mounted on a T-wall or metal pipe

- CAT6 UTP cable length: estimated 40 meters per camera

- Cable containment: PVC conduit / cable trays

Each CCTV camera shall be connected from the relevant network cabinet to the camera location using CAT6 UTP cabling.

Please refer to Preliminary Design Layout provided for Electrical/CIS/Fire Alarm trenches& manholes for underground route to each position.

## Fire Detection and Alarm System Specifications

Fire Detection and Alarm System is to include supply, installation, commissioning and all other necessary parts, works, planning and engineering that may arise to complete installation of fully operational Fire Detection and Alarm System in the new EULEX Compound in Mitrovica.

The price offered is to include all actions required.

Required is one Main Addressable Analogue 4-Loop Fire Alarm Control Panel (FACP) which will connect all fire detecting and alerting devices from facilities in the compound and one Repeater/Remote Panel compatible with the Main Panel (FACP).

Buildings/facilities are of different constructions, containers, metal, concrete, wood, etc. and of different types, accommodation, offices, warehouses, recreational, cafeteria, kitchen, etc.

The Main Fire Control Panel (FACP) and the Remote/Repeater Panel are to process all signals coming from the Detectors, Call Points and cabling and raise audible and visual alarms and indications accordingly.

The installation includes underground and aboveground cabling.

The system shall support networking of multiple control panels and repeater panels, with minimum 64 network addresses over RS485 and minimum 16 network addresses over LAN.

General:

The Contractor must be authorized by the Manufacturer of the Brand(s) of the Fire Detection and Alarm System products for installation, service and maintenance of the Fire Detection and Alarm Systems with the used products.

Buildings 1, 2, 3, 4, 5, 6, 7, 8, 12, 13, 14, 15 and 17 are container buildings, where one Optical Smoke Detector is to be approximately in the middle of the ceiling in every container-sized, approx. 2m x 6m, room. Where two or more container-sized rooms are combined into one larger room, also one Optical Smoke Detector is to be approximately in the middle of the ceiling in every container-sized, approx. 2m x 6m, part of the combined larger room. In addition, 3 Optical Smoke Detectors are to be on the ceiling along the corridor area of every floor in most cases.

Estimated quantities of the Fire Detection and Alarm System items:

-Bldg. 1, Ground Floor: 18 Optical Smoke Detectors, 2 Manual Call Points, 4 Sounders/Flash.

-Bldg. 1, First Floor: 18 Optical Smoke Detectors, 2 Manual Call Points, 3 Sounders/Flash.

-Bldg. 2, Ground Floor: 18 Optical Smoke Detectors, 2 Manual Call Points, 4 Sounders/Flash.

-Bldg. 2, First Floor: 18 Optical Smoke Detectors, 2 Manual Call Points, 3 Sounders/Flash.

-Bldg. 3, Ground Floor: 18 Optical Smoke Detectors, 2 Manual Call Points, 4 Sounders/Flash.

-Bldg. 3, First Floor: 18 Optical Smoke Detectors, 2 Manual Call Points, 3 Sounders/Flash.

-Bldg. 4, Ground Floor: 8 Optical Smoke Detectors, 2 Manual Call Points, 3 Sounders/Flash.

-Bldg. 4, First Floor: 8 Optical Smoke Detectors, 2 Manual Call Points, 2 Sounders/Flash.

-Bldg. 5, Ground Floor: 10 Optical Smoke Detectors, 2 Manual Call Points, 3 Sounders/Flash.

-Bldg. 5, First Floor: 10 Optical Smoke Detectors, 2 Manual Call Points, 2 Sounders/Flash.

-Bldg. 6, Ground Floor: 15 Optical Smoke Detectors, 2 Manual Call Points, 3 Sounders/Flash.

-Bldg. 6, First Floor: 15 Optical Smoke Detectors, 2 Manual Call Points, 2 Sounders/Flash.

-Bldg. 7: 1 Sounder/Flash. (this is just a group of sea containers).

-Bldg. 12: 9 Optical Smoke Detectors, 2 Manual Call Points, 3 Sounders/Flash.

-Bldg. 13, Ground Floor: 2 Optical Smoke Detectors, 1 Sounder/Flash.

-Bldg. 13, First Floor: 2 Optical Smoke Detectors.

-Bldg. 14: 11 Optical Smoke Detectors, 2 Manual Call Points, 3 Sounders/Flash.

-Bldg. 15, Ground Floor: 25 Optical Smoke Detectors, 2 Manual Call Points, 4 Sounders/Flash.

-Bldg. 15, First Floor: 25 Optical Smoke Detectors, 2 Manual Call Points, 3 Sounders/Flash.

Bldg. 8: 5 Optical Smoke Detectors, 2 Manual Call Points, 3 Sounders/Flash.

-Bldg. 9: 5 Optical Smoke Detectors, 2 Manual Call Points, 4 Sounders/Flash.

-Bldg. 10: 10 Optical Smoke Detectors, 3 Manual Call Points, 4 Sounders/Flash.

-Bldg. 11: 9 Optical Smoke Detectors, 2 Heat/temperature Detectors, 4 Manual Call Points, 4 Sounders/Flash.

-Bldg. 16, Ground Floor: 17 Optical Smoke Detectors, 5 Heat/ Temperature Detectors, 7 Manual Call Points, 8 Sounders/Flash.

-Bldg. 16, First Floor: 19 Optical Smoke Detectors, 2 Manual Call Points, 5 Sounders/Flash.

- Bldg. 17: 6 Optical Smoke Detectors, 2 Manual Call Points, 3 Sounders/Flash.

-Bldg. 18: 1 Optical Smoke Detector, 1 Manual Call Point, 1 Sounder/Flash (Fuel Station Cabin).

-Bldg. 19: NIL (this is just a group of sea containers under roof cover).

Heating Plants: 2 Heat/Temperature Detectors, 1 in each of the two plants and one (1) Sounder/Flash at each.

IN TOTAL 329 Detectors of which 320 Smoke Detectors and 9 Heat Detectors.

IN TOTAL 55 Manual Call Points.

IN TOTAL 85 Sounders/Flash.

Codes and Standards

All equipment supplied as part of the fire detection and alarm system shall conform to the following standard:

EN54 -European Standard for Fire Detection and Alarm Systems for Buildings.

All detection devices shall be independently certified as complying with the relevant EN54 standard.

The Fire Alarm Control Panel shall be independently certified as complying with requirements of EN54-2 (Control and Indication) and EN54-4 (Power Supply).

Fire Alarm Control Panel (FACP):

Addressable Analogue 4-Loop Fire Alarm System Control Panel with item capacity of at least 120 items per Loop.

Compliant to EN54 (EN54-2, EN54-4).

Supply, installation and commissioning including all parts necessary for operation for FACP, including such as: cabling, labor, any other works related issues and parts to complete the whole system must be included in price. Location: Building 13, Security Reception.

Functional Description:

The FACP shall be the central controller of the complete system. It shall receive and process information from the detection devices, call points and cabling, provide audible and visual indication of alarm and other conditions to the user, automatically initiate alarm response sequences and provide the user interface for interrogation and user programming of the system.

Updates to the FACP operating software shall be simple to undertake and shall not require the use of replaceable components. The operating program and configuration memory shall be stored in non-volatile memory and shall not rely on batteries for retention.

The FACP shall be able to be easily configured to meet the exact detection zone and cause/effect output requirements of the buildings.

Operating programs and configuration data shall be stored in a non-volatile memory and fully configurable on-site by means of upload/download of PC configuration software.

The FACP shall interrogate each addressable detection device and provide alarm indication within 3 seconds of a Manual Call Point operation and within 10 seconds for all other devices.

The FACP shall continuously scan all connected loop devices and process alarm events within EN54 required response times.

The system shall be capable of scanning and processing all connected devices within less than 1 second under normal operating conditions.

The FACP shall have the ability to annunciate an alert or pre-alarm condition designed to give the earliest possible warning of potential fire condition without raising the full alarm condition. The FACP shall have, as standard, automatic drift compensation to prevent false alarms due to detector contamination and shall give warning when compensation limits are reached. The system shall support detector diagnostics and predictive maintenance indication for degraded or contaminated detectors.

Operating programs, configuration data, response sequences, etc. shall be in English language. The FACP shall provide a user interface from which; controls can be operated, manual operations can be carried out, indications are audible and visible and system information can be obtained. It shall also be capable of unambiguously indicating the following functional conditions: Quiescent condition, fire alarm condition, fault warning condition and disabled condition. Furthermore, the fire alarm condition shall always be capable of clearly being indicated without any prior manual intervention at the FACP. The FACP shall be easy to configure on all basic operating characteristics and variables through the user interface on the FACP to satisfy the detection zone and output mapping of the premises. The FACP shall support up to around 500 detectors, manual call points and alarm sounders/flash. The FACP shall incorporate a real-time clock for time stamping of events in the event history log and for scheduling of time related functions. It shall be possible to select device modes for both active and inactive time periods for multi-sensor detectors. It shall be possible to connect optional equipment in accordance with the requirements of EN54-2 standardised I/O such as mimic panels and remote/repeater control panels. The system shall support RS485 and/or TCP/IP networking for repeater panels, supervision software and remote monitoring.

Panel Construction:

The FACP shall be of metal construction. Sufficient knockouts/openings shall be provided to accommodate all likely wiring requirements. It shall not be possible to open the enclosure without a key or special tool.

Fire Alarm Panel - Indications

The FACP shall be equipped with a graphics display. The display shall incorporate an LED backlight that will illuminate upon any event or button press. The primary display shall be simultaneously capable of indicating the presence of Fire Alarms, Faults, Disablements and Tests in accordance with the requirements of EN54-2. In addition, the following minimum LED indicators shall be provided in accordance with the requirements of EN54-2:

Power On	Green

Pre Alarm                      Yellow

Fire Alarm	Red

Fault	Yellow

Disabled or Out of Service	Yellow

Test	Yellow

Battery Fault	Yellow

System Fault	Yellow

Evacuation	Yellow

Additional programmable status indications shall be supported either by programmable LEDs, LCD messages, programmable outputs, or software-configurable event indications.

Panel Controls:

The FACP shall have the following minimum manual controls:

Silence Buzzer

Evacuate (Sound Alarms)

Silence / Resound Alarms

Reset

In addition, shall have the controls for menu operation and programming:

Navigation keys,

A confirmation key,

A numeric keypad, 0-9, also providing the function for letter/ character programming

A cancel key

A menu select key

•Remote/Repeater Panel:

- Addressable Analogue Remote/Repeater Control Panel compatible with the 4-Loop Main Control Panel (FACP).

- It shall be possible to provide remote access to monitor (Remote Display Terminal) or monitor/control (Remote Control Terminal) operation of the installation.

- The Remote Display Terminal shall provide the same display, indications and navigation buttons as the FACP, except for restricted control functions according to access level authorization.

- Remote control functionality shall provide the capability to silence alarms, resound alarms, activate evacuation and reset the system. In addition, it shall be possible to remotely enable or disable zones and points and remotely configure zone walk tests.

- The remote/repeater panel shall provide remote visualization of events, alarms, faults, disabled conditions and system status.

- The repeater panel shall include a backlit alphanumeric graphic display, minimum 128 × 64 pixels.

- The repeater panel shall support RS485 and/or TCP/IP LAN connection to the main Control Panel (FACP).

The system shall support networking of multiple control panels and repeater panels, with minimum 64 network addresses over RS485 and minimum 16 network addresses over LAN.

Location: Guard Cabin, about 5 meters from Building 13 at gate area.

Power Supplies:

Power supplies integral to the FACP or Remote/Repeater Panel shall be certified to EN54-4: and shall be capable of supporting 72 –hour standby requirements.

FACP Power supplies shall be capable of operating from a main supply. Secondary Power: The system power supply shall be provided with an integral uninterruptible power source ‘UPS’/backup battery system. This UPS/backup battery system shall provide continuous power to the system in the event of a commercial power failure. Transfer from commercial to standby power shall be instantaneous to ensure proper processor operation and indicated by flashing of the system power LED. Loss of commercial power shall be annunciated as a system trouble. System trouble shall be indicated for any abnormal power condition. The system shall automatically reset upon the return of normal power. No operator intervention shall be required.

Cabling:

Fire Alarm Cabling to be drawn underground in the prepared piping, estimated approximately 4000 meters. Aboveground into buildings estimated approximately 4500 meters. Designed to meet the EU standards/requirements.

- Standard Fire Cable

- Consisting of four (4) Cores

Fire resistant twisted and shielded cable suitable for addressable loop communication in accordance with manufacturer requirements and EN54 standards.

Minimum conductor size shall be selected according to loop length and voltage drop calculations.

The loop design shall include short-circuit isolation in accordance with EN54 and other applicable standards. Maximum loss in case of short circuit shall not exceed 32 devices. Isolation is to be in place for group of all Detectors (8-25 Detectors) on each floor of 2-storey buildings for easy fault-fnding.

Fault Reporting:

The FACP shall monitor system components and interconnections in accordance with EN54-2, such that a failure shall cause a fault indicator to light up and a message is to be shown on the alphanumeric display.

To help faultfinding and repair, the FACP shall provide messages in display to indicate the location of where a fault has occurred in the system.

System Management:

The FACP shall incorporate the following end user system management facilities: an event log capable of storing up to the last 999 events. These events shall be individually time and date stamped. It shall be possible to view the content of the event log.

Events shall be displayed in chronological order with the newest events first. It shall be possible to scroll through the events when viewed on the LCD display.

The FACP shall be capable of disabling an individual detector, a group and or zone for maintenance purposes.

The FACP shall have a facility to enable the user to easily change the time and date settings of the system ‘real time’ clock. It shall also be possible for the user to change the alphanumeric message text.

Panel Sounder Control:

All fire conditions shall visually and audibly indicate on all panel displays immediately upon receipt of the signal but the FACP shall also have the ability to delay all sounders. A sounder/relay output delay of up to 10 minutes shall be possible from all smoke and heat devices. Call Points and Evacuate signals shall automatically override any delay.

Detectors – General:

Detectors shall comply with and be type certified to EN54-7 or EN54-7 and EN54-17 for Smoke Detectors and EN54-5 for Heat Detectors.

Each detector shall have its own mounting base which, with the exception of isolating bases/isolator, will not contain any electronic components.

Alarm LEDs shall be provided on each detector. The LEDs will be controlled by the FACP, independently of the device. LEDs shall be capable of being reset by the FACP without removing power from the loop.

Detectors shall be capable of being remotely tested from the FACP by transmission of a single bit in the communication protocol.

The loop design shall include short-circuit isolation/insulation in accordance with EN54 requirements. In case of short circuit, the maximum loss of devices shall not exceed 32 devices between isolators/insulators.

Isolators/Insulators are to be installed for Detector group of all Detectors (8-25 Detectors) on each floor in 2-storey buildings for easy fault-finding.

The FACP shall recognize response as a test signal and will not raise a general alarm.

Manual Call Points (MCP):

Each MCP installed on the loop shall have a unique address.

The elapsed time between activation of the MCP and initiation of the sounders in an alarm condition via command from the FACP shall not exceed three (3) seconds.

System Installation Wiring/Cabling Diagrams:

The complete fire alarm system shall be tested by the specialist Installer and a certificate issued to this effect.

The Installer shall ensure that the ‘as fitted’ drawing shows details of the route of the loop circuits and the device label numbers and shall provide cable test certification.

Zone/Loop Designation:

All cabling shall be installed to cover all fire alarm system equipment. The devices shall be connected and wired sequentially and marked on the “as fitted” drawings to assist future engineering functions.

Device Labels:

Any “user guide”, “labeling”, “instructions", "leaflets”, etc. shall be in English language.

Programming of System:

Properly programmed fire alarm system is to be be provided.

Inspection, Testing and Commissioning:

An audibility test of the alarm devices shall be taken in each location. All trigger devices ie: manual call points, heat and smoke detectors shall be tested for correct operation. Mains failure test shall be carried out to verify correct operation of the back-up battery system. A certificate of installation and cable test certificates of the system should be provided

Fire Designation Drawing:

Each fire compartment/zone shall be easily identified by means of clearly marked color codes. The fire zone chart shall be as a minimum sized A3 and colored up for handover on completion of the works.

Warranty:

The contractor shall provide two (2) years' written warranty for all equipment and mechanical and electrical defects per the project’s warranty requirements.

Demonstration and instructions:

Provide sufficient demonstration and repeat demonstrations if required for fire alarm user.

Demonstrate normal and abnormal modes of operation, and required responses to each. Instructions must be supported with instruction manual for the operation of the system.

Manual Call Point, connected to the Fire Alarm Panel                                                             Quantity: Fifty-five (55)

Designed and certified in accordance with EN54-11 or EN54-11 and EN54-17.

• Addressable Manual Call Point compatible with the FACP.

• Integrated short-circuit isolator, certified according to EN54-17.

• Surface mountable.

• Resettable by key, without break glass.

• Supplied complete with reset/test key.

• Supplied with transparent protective lift-up cover.

• Housing: red ABS plastic or equivalent corrosion-resistant material.

• LED status indication.

• Protection rating minimum IP40.

• Operating temperature range minimum -10°C to +70°C.

• Supply, installation and commissioning, including all parts necessary for operation, must be included in the price.

Fire alarm Sounder/Flash - connected to the Fire Alarm Panel                                                              Quantity: Eighty-five (85)

• Designed and certified to meet the requirements of EN54-3.

• Loop-powered fire alarm sounder with flashing light upon activation, compatible with the FACP.

• FACP powered 12–28VDC.

• Color: red.

• Housing: ABS plastic or equivalent.

• Sound output: minimum 90 dB at 1 meter.

• Including optical visual alarm/flashing light/LED indication.

• Suitable for indoor installation.

• Supply, installation and commissioning including all parts necessary for operation must be included in the price.

Fire Alarms per Building, Sounder Grouping

Configuration of the fire alarm system so that, in case of detection, in addition to the FACP, the alarm is activated only in/at the specific building where the fire alarm has been triggered/the building where was the detection. Grouping/dividing of alarm zones, cabling and the necessary equipment for full functionality of the alarm per building feature. Fourteen (14) buildings are designated for this feature: buldings 1-6, 8-12 and 14-16. This feature includes installation of one (1) sounder on the external wall of each 14 buildings.

Supply, installation and commissioning, including all equipment and parts necessary for this operation of this feature must be included in the price.

Necessary equipment and parts for the feature in each desinated building, such as:

- Loop Input/Output interface Module  - double supervised output.
- 5 Amp Power Supply in a case with operational recharge and fault status Led signalling/Relay Outputs. Certified EN 54-4 CPR.  
Including a Set of Batteries of two (2) pieces 12V 7A.

Smoke Detector - connected to the Fire Alarm Panel

Quantity: Three hundred and twenty (320)

• Detectors shall comply with and be certified according to EN54-7 or EN54-7 and EN54-17.

• Addressable Analogue Optical Smoke Detector compatible with the FACP.

• Maximum quantity for Loop more than 120.

• Loop-powered directly from the addressable detection loop.

•LED indicating power on and alarm activation.

•LED visibility 360 degrees.

•With Base.

•Color: white.

Supply, installation and commissioning, including all parts necessary for operation must be included in the price.

Heat Detector - connected to the Fire Alarm Panel

Quantity: Nine (9)

• Detectors shall comply with and be type certified to EN54-5.

• Addressable Analogue Heat/Temperature Detector.

• Power Supply 20-28V DC from Loop.

• Detector operation shall include both fixed temperature and rate-of-rise detection modes.

• Fixed temperature threshold and thermovelocimetric response shall be individually selectable or configurable.

• Available with integrated isolator or external loop isolator where required by loop design.

• LED alarm indication with 360° visibility.

• Degree of protection minimum IP20.

• Operating temperature range minimum -10°C to +70°C.

• Application: Indoor use.

• With Base.

• Color: white.

• Supply, installation and commissioning, including all parts necessary for operation must be included in the price.

## Firefighting Network Specifications – External Overground Hydrants

The Contractor shall design, supply, install, test, and commission a complete and fully operational Above Ground Fire Hydrant System for the new EULEX Centre Mitrovica.

The Contractor shall be fully responsible for:

All engineering design (hydraulic calculations, layout drawings, details)

Selection of materials, equipment, and components

Compliance with applicable standards and codes

Provision, installation, testing, and commissioning

Submission of drawings, technical data sheets, and as-built documentation

The system shall include, but not be limited to, hydrants, cabinets, hoses, nozzles, tools, piping network, civil works, and all accessories necessary for a complete and operational installation.

Pipes:

OD 110 PE pipe, PN16 (Standards EN 12201-2 / ISO4427 / DIN8074) shall be provided and installed throughout the trench with all necessary connections including connection to the city water line at the main manhole.  Final designs shall confirm the pipe diameter and pressure rating as per standard.

Above Ground Fire Hydrant:

DN80 Above Ground Fire Hydrant PN16 Rd (m) 1.0, in accordance with  DIN EN 14384 (formerly DIN 3222) and DIN EN 1074-6 including all labour, works and components/parts necessary for installation and operation of the fire hydrant.

- The hydrant shall be equipped with two (2) Storz couplings of steel or aluminium with covers, of size Ø 66 mm between coupling lugs and one (1) larger Storz coupling of steel or aluminium with cover, of size Ø 89 mm between coupling lugs.

Outdoor Fire Hydrants Cabinet:

- Constructed of steel/metal sheet.

- Painted in red color.

- Dimensions 540x1080/1060x185 mm.

- Free standing on metal legs/supports.

- With fixed metal holders inside to hold two (2) flat rolled fire hose rolls.

- With metal door with closing mechanism.

Fire Hoses in Fire Hydrant Cabinet:

- Hose inner diameter Ø 52 mm

- Hose length fifteen meters (15 m)

- With fixed Storz coupling of steel or aluminium on both ends of size Ø 66 mm between coupling lugs.

- Outer hose jacket with one or two layers.

- Inside of hose rubber lined.

- Bursting pressure up to 50 bar.

- Light weight and flexible.

- Rolled flat, rolls hanging on metal holders inside cabinet.

Supply of Fire Hose Nozzles in Fire Hydrant Cabinet:

- With nozzle head aperture diameter Ø 10-12 mm.

- Adjustable water flow by operating handle/hand valve.

- With Storz coupling of steel or aluminium of size Ø 66 mm between coupling lugs to connect to Ø 52 mm fire hose.

Set of Tools in Fire Hydrant Cabinet:

- Opening/closing tool of steel for the two (2) smaller sizes of Storz couplings and their covers, two (2) pieces.

- Opening/closing tool of steel for the one (1) larger size Storz coupling and its cover, one (1) piece.

- Opening/closing tool of steel for the Hydrant Water Valve, one (1) piece.

- Any other tools necessary for the operation of the Fire Hydrant and opening/closing any couplings or covers.

Hydrants shall be positioned such that the coverage ensures that all areas can be reached by firefighting hoses in accordance with applicable international standards and Administrative Instruction 24/2012.

Testing and Inspection of the pipeline and installed Fire Water Hydrants shall take place, taking into consideration the set requirements under Administrative Instructions on the Networks of the hydrants for firefighting 24/2012 of MIA, or its replacement/amendment.

Written reports based on the test results shall be presented to the Project Manager of EULEX.

Testing shall be done using proper/ specialized equipment to conduct fire hydrant testing (water flow test, volume, pressure, etc.) and inspection.

The test shall be carried out in sections. Each section to be tested shall have been backfilled except at the joints, which shall be left open for inspection, unless the EULEX Project Manager has ordered completion of backfill before testing.

The Contractor shall provide the necessary test pumps and pressure gauges (to record bars) and shall make such temporary connections as may be required for testing the line.  The test shall be made in the presence of the Project Manager.

All equipment, labour, materials necessary for the carrying out of these tests to the complete satisfaction of the EULEX Representative shall be provided by the Contractor at his own expense.

Should any test fail, the Contractor shall, after repairing of any leaks, carry out further tests, all as described above until such tests meet with the requirements contained herein.

Connection to the City network:

For the new fire hydrant network to be connected, EULEX through Water Department will establish a connection point inside the Compound (Manhole with water meter) where the Contractor is to connect the newly installed pipeline, accordingly, see the dwg provided for the position of the connection point.

Contractor is to provide all the required materials/accessories for establishing the connection to the main water meter.

Additional to the obligations deriving from the contract during the defects liability period the Contractor is to test/control the network of hydrants at least once a year as per Administrative Instructions 24/2012 On the Network of the Hydrants for Firefighting, or its replacement/amendment.

## Solar Photovoltaic System Specifications

This part of the project is intended to contribute to the reduction of greenhouse gas emissions and the mitigation of climate change by utilizing renewable solar energy.

- System Capacity: 260 kWp (±3%)

- System type: with zero-export device / no energy is fed back into the grid.

- Online monitoring

A site assessment will be conducted to evaluate solar viability, including shading analysis, orientation, and the energy requirements of the facilities.

Based on this assessment, a detailed system design will be prepared, incorporating engineering layouts, performance modeling, and a comprehensive list of materials with technical specifications.

These will include solar panels, inverters, mounting systems, the zero-export device, wiring, disconnect switches, combiner boxes, surge protectors, grounding equipment, etc.

All drawings and specifications will be submitted to the Project Manager for approval prior to the commencement of construction.

Following approval, the building phase will begin with the provision and installation of all materials in accordance with the approved design.

Panel positioning is be carefully selected based on orientation and functional use, with installations proposed to be in Training Building, Gym, Reserve Block, parking covers, and other designated areas.

The project will be executed in compliance with reference standards (IEC, IEEE, NEC).

The same underground route for Electricity, CIS, and Fire Alarm System will be utilized for cabling, with cables placed in ducting to reach each building and installation point.

Upon completion, the system will be commissioned and fully tested to ensure that performance meets design expectations, delivering reliable renewable energy to the facilities while supporting sustainability and climate change mitigation goals.

# Testing and Commissioning

Upon completion of all construction works, the Contractor shall carry out comprehensive testing and commissioning of the entire compound to verify that all systems, components, and installations are functioning correctly and in accordance with the design specifications and applicable standards.

This shall include, but not be limited to, the inspection and functional testing of civil, architectural, structural, electrical, mechanical, and any specialized systems to ensure proper performance, safety, and operational readiness.

Any defects or deficiencies identified during testing shall be promptly rectified by the Contractor prior to Provisional Acceptance.

The Contractor shall submit all relevant test reports to the EULEX Project Manager.

Provisional Acceptance of the works shall only occur after successful completion of all testing, commissioning, and rectification works to the satisfaction of the Contracting Authority.

# Handover

Handover/Provisional Acceptance shall include submission of all required documentation, including:

- As-built drawings (all disciplines)

- Operation and maintenance (O&M) manuals containing manufacturer instructions and spare parts lists.

- Test and commissioning reports

- Warranties, and any relevant certificates.

- On site training for operators and maintenance staff on system operation, emergency procedure and maintenance procedures

The Contractor shall ensure that the works are complete, fully operational, clean, and free from defects at the time of Handover/Provisional Acceptance.

A joint inspection shall be carried out with the Contracting Authority Representative, Project Manager & Engineer, to confirm that all works comply with the contract requirements.